## 119_151
S&C Power Fuses - Type SMD-1A (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-1A (34.5 and 46 kV)
Slow Speed (TCC 119-1-5-1) | [9 empty] | Slow Speed (TCC 119-1-5-1) | [9 empty] | Slow Speed (TCC 119-1-5-1)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
23502.3 | 0.015903 | 23502.3 | 0.015903 | 23502.3 | 0.015998 | 23502.3 | 0.015998 | 23502.3 | 0.016093 | 23502.3 | 0.016093 | 23502.3 | 0.016302 | 23502.3 | 0.016498 | 23502.3 | 0.016896 | 23714.5 | 0.017063 | 23714.5 | 0.018381 | 23700.9 | 0.0197 | 23714.5 | 0.02199
22468.1 | 0.016302 | 22739.3 | 0.016206 | 22944.9 | 0.016206 | 23408.4 | 0.015998 | 22876.2 | 0.016302 | 22200 | 0.016696 | 22922 | 0.016498 | 22899.1 | 0.016796 | 23106.1 | 0.017099 | 21367.3 | 0.018182 | 21912.6 | 0.019177 | 21950.3 | 0.020447 | 21700.3 | 0.022994
21033 | 0.016896 | 21308.2 | 0.016796 | 21522.4 | 0.016796 | 21979.1 | 0.016597 | 21436.4 | 0.016896 | 20761.3 | 0.017304 | 21500.8 | 0.017099 | 21457.9 | 0.017407 | 21673.5 | 0.017792 | 18623.5 | 0.02003 | 18795 | 0.021296 | 18741.2 | 0.022771 | 17912.3 | 0.026246
19610.9 | 0.017598 | 19887.4 | 0.017494 | 20087.3 | 0.017407 | 20554.7 | 0.017201 | 20007.1 | 0.017598 | 19338.3 | 0.018005 | 20067.2 | 0.017792 | 20027.1 | 0.018203 | 20248.7 | 0.018605 | 15665.9 | 0.022745 | 15594.3 | 0.024729 | 16120.9 | 0.025711 | 15372.6 | 0.029788
18175.7 | 0.018293 | 18450.4 | 0.018203 | 18654.5 | 0.018095 | 19126.7 | 0.017898 | 18580 | 0.018293 | 17905 | 0.018791 | 18635.8 | 0.018605 | 18598.6 | 0.018997 | 18823.1 | 0.019494 | 12401.8 | 0.027383 | 12894.2 | 0.029146 | 13444.7 | 0.030269 | 13701.2 | 0.033098
16744.7 | 0.019092 | 17031.8 | 0.018997 | 17220.2 | 0.018903 | 17691.5 | 0.018698 | 17151.4 | 0.019092 | 16478.9 | 0.019708 | 17202.9 | 0.019494 | 17168.6 | 0.020004 | 17393.2 | 0.020507 | 10231.1 | 0.0322 | 11034.4 | 0.033652 | 11225.6 | 0.035881 | 11322.5 | 0.040189
15318.7 | 0.020004 | 15597 | 0.019905 | 15801 | 0.019806 | 16266 | 0.019494 | 15722.2 | 0.020004 | 15045.4 | 0.020691 | 15769.5 | 0.020406 | 15738 | 0.021002 | 15959.9 | 0.021702 | 8474.22 | 0.038127 | 9628.53 | 0.038632 | 9192.11 | 0.044147 | 9829.09 | 0.047368
13888.6 | 0.021002 | 14169.2 | 0.020794 | 14369 | 0.020691 | 14836.2 | 0.020507 | 14297.3 | 0.021107 | 13627.2 | 0.021897 | 14340.3 | 0.021509 | 14311.6 | 0.022292 | 14527.9 | 0.023103 | 7035.13 | 0.045742 | 8272.83 | 0.045716 | 7719.01 | 0.053882 | 8483.93 | 0.05683
12466.7 | 0.022203 | 12731.3 | 0.022006 | 12936.7 | 0.02181 | 13397.5 | 0.021594 | 12859.3 | 0.022292 | 12195.4 | 0.023195 | 12910.8 | 0.022807 | 12885 | 0.023708 | 13106 | 0.024693 | 5979.17 | 0.054347 | 6998.96 | 0.05567 | 6545.39 | 0.066905 | 6974.95 | 0.074297
11034.8 | 0.023497 | 11302.9 | 0.023311 | 11508.2 | 0.023103 | 11965.9 | 0.022807 | 11439.3 | 0.02359 | 10762.4 | 0.024792 | 11485.2 | 0.024401 | 11450.8 | 0.025491 | 11670.5 | 0.026789 | 5154.98 | 0.064386 | 5884.06 | 0.069801 | 5711.43 | 0.081566 | 6089.75 | 0.090371
9602.8 | 0.024989 | 9875.49 | 0.024792 | 10075 | 0.024595 | 10538.7 | 0.024208 | 10004.7 | 0.025289 | 9328.3 | 0.026789 | 10054.8 | 0.026288 | 10024.7 | 0.027709 | 10247.7 | 0.029411 | 4505.91 | 0.076543 | 4989.44 | 0.087019 | 4912.88 | 0.10186 | 5172.73 | 0.11627
8174.72 | 0.026896 | 8449 | 0.026603 | 8645.59 | 0.026393 | 9107.08 | 0.026002 | 8576.7 | 0.027299 | 7901.44 | 0.029207 | 8628.31 | 0.028689 | 8593.87 | 0.030603 | 8811.43 | 0.032905 | 3970.27 | 0.090682 | 4452.05 | 0.10327 | 4050.65 | 0.13751 | 4495.6 | 0.14503
6739.84 | 0.029207 | 7014.92 | 0.02889 | 7214.12 | 0.028604 | 7683.25 | 0.028097 | 7142.33 | 0.029912 | 6469.08 | 0.032612 | 7199.7 | 0.031907 | 7163.79 | 0.034683 | 7381.97 | 0.037889 | 3569.12 | 0.10584 | 4022.91 | 0.11992 | 3504.31 | 0.174 | 4071.58 | 0.17104
5312.3 | 0.032193 | 5584.68 | 0.031812 | 5783.62 | 0.031497 | 6252.82 | 0.030908 | 5714.62 | 0.033498 | 5043.11 | 0.037589 | 5766.29 | 0.036486 | 5731.79 | 0.040901 | 7264.8 | 0.038496 | 3144.84 | 0.12816 | 3514.36 | 0.14848 | 3150.25 | 0.20816 | 3643.46 | 0.20626
3884.56 | 0.036413 | 4153.75 | 0.035804 | 4353.65 | 0.035485 | 4821.19 | 0.034683 | 4284.54 | 0.038919 | 3611.07 | 0.046585 | 4336.27 | 0.044284 | 5523.58 | 0.042096 | 6979.93 | 0.039819 | 2703.59 | 0.16291 | 3036.88 | 0.18809 | 2804.52 | 0.25406 | 3157.47 | 0.26431
2452.2 | 0.043198 | 2726.42 | 0.04239 | 2924.12 | 0.041888 | 3390.58 | 0.04082 | 2854.78 | 0.049594 | 3532.49 | 0.047285 | 4263.17 | 0.044993 | 5285.8 | 0.043716 | 6639.5 | 0.041598 | 2384.93 | 0.20032 | 2677.4 | 0.23275 | 2483.9 | 0.31583 | 2801.31 | 0.32743
1023.2 | 0.061891 | 1295.57 | 0.059186 | 1494.75 | 0.057505 | 1960.06 | 0.054178 | 2778.72 | 0.050488 | 3421.24 | 0.048377 | 4112.42 | 0.046217 | 5038.07 | 0.045397 | 6334.64 | 0.043284 | 2102.62 | 0.24746 | 2287.29 | 0.30691 | 2183.61 | 0.40171 | 2479.63 | 0.41149
969.419 | 0.063574 | 1233.62 | 0.060795 | 1456.39 | 0.058426 | 1921.24 | 0.054882 | 2653.79 | 0.052016 | 3260.89 | 0.050089 | 3955.12 | 0.047615 | 4787.55 | 0.047379 | 5847.59 | 0.046678 | 1891.26 | 0.29876 | 1976.52 | 0.39896 | 1906.49 | 0.51712 | 2338.94 | 0.45564
885.978 | 0.066811 | 1144.47 | 0.063511 | 1374.32 | 0.060313 | 1844.06 | 0.056318 | 2514.28 | 0.053909 | 3074.05 | 0.052275 | 3739.71 | 0.049692 | 4499.73 | 0.050089 | 5496.03 | 0.049594 | 1671.21 | 0.37246 | 1722.71 | 0.51328 | 1656.92 | 0.6722 | 1992.43 | 0.61616
820.315 | 0.069796 | 1060.71 | 0.066414 | 1294.28 | 0.062571 | 1762.91 | 0.057906 | 2377.34 | 0.056095 | 2912.45 | 0.05461 | 3543.11 | 0.051912 | 4241.91 | 0.052902 | 5170.78 | 0.052692 | 1474.23 | 0.46834 | 1504.94 | 0.66075 | 1489.51 | 0.82799 | 1737.58 | 0.80693
765.619 | 0.072914 | 975.253 | 0.070213 | 1191.18 | 0.066019 | 1668.57 | 0.060074 | 2225.5 | 0.059127 | 2737.35 | 0.057391 | 3360.2 | 0.054178 | 3982.9 | 0.056095 | 4830.84 | 0.056486 | 1280.52 | 0.61159 | 1302.71 | 0.87379 | 1326.8 | 1.0513 | 1529.27 | 1.0489
701.121 | 0.077162 | 886.865 | 0.074896 | 1100.7 | 0.069588 | 1560.43 | 0.062821 | 2070.89 | 0.062509 | 2567.64 | 0.060614 | 3174.02 | 0.05688 | 3709.91 | 0.060194 | 4554.05 | 0.060074 | 1080.86 | 0.85155 | 1146.53 | 1.1255 | 1199.59 | 1.2994 | 1373.97 | 1.3099
634.397 | 0.082883 | 807.294 | 0.08029 | 974.278 | 0.076172 | 1453.48 | 0.066217 | 1944.44 | 0.065823 | 2403.64 | 0.064209 | 3010.17 | 0.059777 | 3469.47 | 0.0644 | 4149.6 | 0.066811 | 930.277 | 1.1582 | 1012.55 | 1.453 | 1066.72 | 1.6949 | 1223.88 | 1.6795
572.877 | 0.089738 | 744.478 | 0.08573 | 853.794 | 0.084462 | 1349.8 | 0.070004 | 1814.79 | 0.069865 | 2241.13 | 0.068491 | 2806.65 | 0.0637 | 3234.91 | 0.069519 | 3830.55 | 0.073277 | 806.19 | 1.5554 | 875.989 | 2.0069 | 961.694 | 2.1497 | 1092.06 | 2.1794
509.62 | 0.098913 | 685.864 | 0.091995 | 761.8 | 0.09384 | 1267.38 | 0.073715 | 1688.71 | 0.074525 | 2100.08 | 0.072914 | 2637.92 | 0.067612 | 2971.29 | 0.076323 | 3582.3 | 0.079496 | 696.656 | 2.1595 | 775.844 | 2.6585 | 865.022 | 2.7895 | 967.771 | 2.917
456.989 | 0.10968 | 637.577 | 0.098228 | 692.757 | 0.10282 | 1169.93 | 0.078788 | 1557.31 | 0.080369 | 1936.68 | 0.079102 | 2410.86 | 0.074082 | 2742.83 | 0.083877 | 3313.49 | 0.087711 | 613.138 | 2.892 | 662.419 | 3.9559 | 776.733 | 3.6974 | 888.621 | 3.6344
412.26 | 0.12186 | 586.206 | 0.10656 | 624.952 | 0.11446 | 1085.39 | 0.084211 | 1433.27 | 0.08719 | 1785.98 | 0.086242 | 2218.83 | 0.081011 | 2547.18 | 0.09163 | 3098.75 | 0.095914 | 551.504 | 3.7572 | 593.447 | 5.3802 | 709.134 | 4.7406 | 791.098 | 5.0431
362.001 | 0.14074 | 535.75 | 0.11734 | 560.971 | 0.12934 | 983.087 | 0.092544 | 1316.47 | 0.095533 | 1661.91 | 0.093561 | 2075.03 | 0.087363 | 2325.61 | 0.10282 | 2877.71 | 0.10593 | 500.058 | 4.9317 | 519.32 | 8.3141 | 651.136 | 6.1201 | 723.076 | 6.631
330.182 | 0.15745 | 496.54 | 0.12743 | 507.585 | 0.14615 | 892.202 | 0.10231 | 1209.19 | 0.10499 | 1558.87 | 0.1007 | 1898.33 | 0.096871 | 2121.19 | 0.11595 | 2565.08 | 0.12455 | 461.533 | 6.3015 | 468.724 | 12.3926 | 602.005 | 7.9783 | 684.398 | 8.1585
293.136 | 0.18385 | 456.532 | 0.14046 | 474.215 | 0.15934 | 793.685 | 0.11618 | 1129.69 | 0.11378 | 1456.39 | 0.10924 | 1734.93 | 0.10838 | 1942.5 | 0.13141 | 2363.12 | 0.14046 | 427.686 | 8.2667 | 441.371 | 16.903 | 556.262 | 10.6538 | 625.551 | 11.7836
253.821 | 0.22425 | 416.82 | 0.15745 | 440.829 | 0.17563 | 731.197 | 0.12819 | 1038.67 | 0.12642 | 1359.28 | 0.11899 | 1598.34 | 0.12041 | 1773.52 | 0.14982 | 2161.88 | 0.16061 | 397.003 | 11.1405 | 420.161 | 23.1607 | 526.205 | 13.2514 | 576.696 | 17.9917
221.544 | 0.27544 | 379.802 | 0.17827 | 400.075 | 0.20084 | 673.628 | 0.14256 | 967.482 | 0.13838 | 1256.02 | 0.13154 | 1466.62 | 0.13525 | 1627.37 | 0.16946 | 1987.69 | 0.18312 | 374.478 | 14.4235 | 402.037 | 34.6412 | 501.492 | 17.3145 | 545.848 | 27.6917
199.86 | 0.32321 | 345.035 | 0.20284 | 363.816 | 0.23058 | 615.647 | 0.15998 | 901.169 | 0.15207 | 1161.77 | 0.14673 | 1383.97 | 0.14702 | 1503.75 | 0.19168 | 1825.71 | 0.20939 | 355.26 | 19.5159 | 389.125 | 47.7112 | 482.615 | 22.0351 | 523.2 | 43.2605
178.504 | 0.39035 | 315.968 | 0.2308 | 334.168 | 0.26262 | 554.834 | 0.18458 | 838.563 | 0.16795 | 1079.98 | 0.16238 | 1296.87 | 0.16125 | 1390.91 | 0.21573 | 1715.95 | 0.23195 | 342.279 | 25.5436 | 377.061 | 71.4838 | 468.456 | 28.5777 | 508.432 | 62.698
162.977 | 0.45488 | 290.8 | 0.26132 | 305.405 | 0.3024 | 506.571 | 0.21065 | 772.541 | 0.18865 | 1007.97 | 0.18005 | 1218.9 | 0.17703 | 1278.84 | 0.24767 | 1568.25 | 0.26922 | 332.237 | 33.0332 | 372.34 | 95.0745 | 456.277 | 36.7671 | 497.203 | 96.7774
150.145 | 0.52431 | 266.302 | 0.30061 | 280.798 | 0.34752 | 450.185 | 0.25114 | 721.752 | 0.20939 | 926.76 | 0.20385 | 1144.47 | 0.19475 | 1179.33 | 0.28265 | 1478.4 | 0.29763 | 321.568 | 47.222 | 368.522 | 132.605 | 447.992 | 46.1261 | 490.416 | 147.51
139.714 | 0.59717 | 247.306 | 0.33833 | 258.431 | 0.39779 | 406.122 | 0.29587 | 668.261 | 0.23614 | 817.04 | 0.24792 | 1068.16 | 0.21659 | 1094.11 | 0.32034 | 1402.08 | 0.32742 | 312.312 | 71.1571 | 365.998 | 175.661 | 439.102 | 61.8776 | 487.058 | 206.804
121.218 | 0.77239 | 226.926 | 0.38919 | 238.8 | 0.45578 | 379.422 | 0.33134 | 623.08 | 0.26314 | 734.862 | 0.29499 | 984.07 | 0.24718 | 1021.16 | 0.36018 | 1303.37 | 0.37292 | 307.344 | 98.1729 | 365.788 | 263.036 | 431.623 | 83.1984 | 485.109 | 273.012
107.833 | 0.962 | 207.601 | 0.45217 | 224.219 | 0.50942 | 340.238 | 0.3974 | 575.748 | 0.29852 | 668.261 | 0.34512 | 923.984 | 0.27408 | 952.125 | 0.40698 | 1217.68 | 0.42306 | 304.541 | 133.826 | 366.417 | 354.683 | 429.158 | 105.76 | 484.831 | 382.096
97.4738 | 1.1653 | 189.164 | 0.53059 | 210.528 | 0.56767 | 309.092 | 0.46957 | 541.134 | 0.33101 | 605.269 | 0.4082 | 860.652 | 0.30847 | 888.64 | 0.45942 | 1129.69 | 0.48667 | 303.323 | 179.423 | 365.998 | 485.158 | 427.441 | 140.26 | 485.665 | 514.93
89.2623 | 1.3921 | 165.771 | 0.67949 | 196.884 | 0.637 | 288.195 | 0.53165 | 502.534 | 0.37478 | 549.313 | 0.4857 | 803.267 | 0.34718 | 824.427 | 0.52275 | 1054.37 | 0.55375 | 301.763 | 251.401 | 366.417 | 597.945 | 426.219 | 186.655 | 486.779 | 596.577
81.3349 | 1.6762 | 148.354 | 0.83048 | 178.861 | 0.76021 | 270.327 | 0.59362 | 465.755 | 0.42728 | 500.528 | 0.57334 | 749.708 | 0.39191 | 765.619 | 0.60074 | 969.419 | 0.65043 | 300.9 | 342.507 |  |  | 425.975 | 255.172
75.1564 | 1.9806 | 134.639 | 0.99801 | 166.435 | 0.8693 | 254.838 | 0.65692 | 429.944 | 0.49201 | 460.199 | 0.66348 | 702.525 | 0.43933 | 723.197 | 0.6648 | 915.705 | 0.73132 | 299.697 | 452.937 |  |  | 425.001 | 330.181
70.2154 | 2.2989 | 122.192 | 1.2089 | 155.805 | 0.99012 | 236.424 | 0.7512 | 398.08 | 0.56318 | 420.589 | 0.77855 | 640.133 | 0.52016 | 675.652 | 0.75195 | 854.649 | 0.84127 | 299.182 | 600.003 |  |  | 425.488 | 473.086
66.2585 | 2.6366 | 110.784 | 1.4805 | 145.416 | 1.1367 | 222.21 | 0.84546 | 368.208 | 0.64464 | 387.475 | 0.90634 | 582.117 | 0.622 | 622.457 | 0.87886 | 803.267 | 0.95723 |  |  |  |  | 425.975 | 598.63
62.3998 | 3.0331 | 99.9415 | 1.8476 | 134.101 | 1.3432 | 206.153 | 0.9745 | 325.591 | 0.81091 | 362.001 | 1.0302 | 532.012 | 0.74009 | 583.282 | 0.9911 | 743.734 | 1.1277
59.1194 | 3.4649 | 93.4645 | 2.136 | 124.785 | 1.559 | 194.341 | 1.0924 | 297.566 | 0.95914 | 337.864 | 1.1781 | 497.534 | 0.84462 | 550.963 | 1.1088 | 698.322 | 1.2832
55.6764 | 4.0136 | 87.3199 | 2.494 | 114.731 | 1.8753 | 183.023 | 1.2307 | 272.226 | 1.1401 | 314.392 | 1.3593 | 468.09 | 0.95344 | 516.288 | 1.2554 | 649.808 | 1.4893
52.1202 | 4.7947 | 82.1523 | 2.8746 | 108.482 | 2.1212 | 173.749 | 1.3701 | 252.303 | 1.3233 | 292.843 | 1.573 | 437.754 | 1.0979 | 491.107 | 1.3879 | 610.131 | 1.7031
49.1339 | 5.6767 | 77.2133 | 3.3399 | 103.088 | 2.359 | 164.121 | 1.5405 | 235.244 | 1.5283 | 276.064 | 1.7792 | 414.741 | 1.2295 | 468.558 | 1.5298 | 577.478 | 1.9187
46.3651 | 6.6678 | 73.7418 | 3.7664 | 98.3551 | 2.608 | 155.493 | 1.7286 | 222.655 | 1.7184 | 257.657 | 2.063 | 394.908 | 1.362 | 444.37 | 1.7167 | 551.515 | 2.1381
44.1478 | 7.7546 | 69.6559 | 4.389 | 93.2777 | 2.9587 | 147.91 | 1.9225 | 209.269 | 1.963 | 242.894 | 2.3637 | 372.653 | 1.5482 | 420.168 | 1.9494 | 527.246 | 2.359
42.2051 | 8.8675 | 66.0601 | 5.074 | 89.2623 | 3.3134 | 139.714 | 2.1875 | 196.687 | 2.2403 | 229.666 | 2.6896 | 355.188 | 1.7235 | 399.276 | 2.1962 | 498.032 | 2.7003
40.6313 | 10.2006 | 62.5247 | 5.948 | 85.0787 | 3.7552 | 132.369 | 2.4841 | 183.023 | 2.6498 | 219.559 | 3.009 | 335.172 | 1.9669 | 381.706 | 2.4498 | 470.907 | 3.0786
39.3123 | 11.7693 | 59.5347 | 6.9796 | 81.8244 | 4.1846 | 126.671 | 2.7654 | 174.271 | 2.9704 | 207.601 | 3.4718 | 322.351 | 2.1509 | 362.726 | 2.7709 | 446.151 | 3.4925
37.8086 | 14.3702 | 56.9149 | 8.1901 | 78.3803 | 4.705 | 120.372 | 3.1404 | 164.286 | 3.4204 | 197.871 | 3.923 | 310.021 | 2.3614 | 344.001 | 3.1812 | 425.666 | 3.9464
36.6544 | 17.6508 | 54.5738 | 9.6009 | 75.5331 | 5.2901 | 114.731 | 3.552 | 155.028 | 3.97 | 189.732 | 4.4152 | 300.257 | 2.5669 | 328.535 | 3.6018 | 408.975 | 4.389
35.6423 | 21.7882 | 52.5914 | 11.2547 | 73.3006 | 5.901 | 110.012 | 3.974 | 148.949 | 4.4416 | 183.206 | 4.8957 | 287.331 | 2.8462 | 313.137 | 4.1146 | 393.331 | 4.9006
35.0064 | 25.9765 | 50.8841 | 13.312 | 70.5673 | 6.8627 | 105.171 | 4.5172 | 144.113 | 4.8618 | 178.147 | 5.3377 | 278.56 | 3.0908 | 299.058 | 4.7426 | 377.908 | 5.4991
34.3132 | 32.6117 | 49.6277 | 15.5124 | 68.1401 | 7.9259 | 101.148 | 5.069 | 138.601 | 5.3963 | 171.504 | 5.9955 | 268.173 | 3.417 | 287.906 | 5.3059 | 363.816 | 6.1158
33.8024 | 39.3077 | 48.354 | 18.6049 | 65.6649 | 9.3283 | 97.3764 | 5.6824 | 133.433 | 5.9836 | 165.937 | 6.6944 | 258.173 | 3.7927 | 278.282 | 5.9599 | 351.653 | 6.7747
33.4325 | 48.4254 | 47.5389 | 21.6372 | 63.5332 | 10.9134 | 94.027 | 6.4017 | 128.2 | 6.7949 | 161.678 | 7.4082 | 249.792 | 4.1639 | 267.637 | 6.7949 | 337.864 | 7.6475
33.1993 | 60.0742 | 46.9718 | 25.2891 | 62.0265 | 12.4549 | 90.9746 | 7.1765 | 123.543 | 7.7392 | 156.899 | 8.3627 | 240.718 | 4.6631 | 259.467 | 7.7009 | 328.535 | 8.4967
33.0668 | 79.0235 | 46.3187 | 29.7044 | 60.5555 | 14.4561 | 88.2857 | 8.077 | 119.772 | 8.7103 | 151.806 | 9.4683 | 233.137 | 5.145 | 251.295 | 8.9382 | 319.782 | 9.4683
33.0007 | 108.271 | 45.812 | 34.7178 | 59.4157 | 16.8122 | 85.8479 | 9.163 | 115.768 | 10.2107 | 147.762 | 10.8378 | 226.246 | 5.6767 | 244.112 | 10.2006 | 313.45 | 10.3435
33.0007 | 153.286 | 45.3108 | 40.901 | 58.5311 | 19.3976 | 83.8959 | 10.3743 | 112.234 | 11.8514 | 143.825 | 12.4301 | 219.779 | 6.2447 | 239.278 | 11.4692 | 304.795 | 11.8161
33.0007 | 221.153 | 44.9048 | 48.5217 | 57.6596 | 23.2645 | 81.5792 | 12.0772 | 109.135 | 13.6739 | 140.555 | 14.2281 | 212.219 | 7.1126 | 233.603 | 12.9597 | 298.759 | 13.1673
33.0007 | 317.486 | 44.547 | 58.659 | 56.9149 | 27.6266 | 79.6445 | 14.0038 | 106.44 | 16.0135 | 136.947 | 16.7455 | 204.715 | 8.1011 | 229.666 | 14.4992 | 291.966 | 14.7902
32.9677 | 467.707 | 44.3691 | 72.481 | 56.2922 | 33.3653 | 77.9114 | 16.0453 | 104.541 | 18.3116 | 133.967 | 19.4168 | 198.466 | 9.2269 | 225.568 | 16.2216 | 285.327 | 16.8791
32.9348 | 545.559 | 44.1478 | 91.6296 | 55.7321 | 40.0964 | 76.8282 | 18.1126 | 102.471 | 21.4021 | 130.268 | 23.5435 | 192.215 | 10.6246 | 221.766 | 18.1847 | 279.677 | 19.0727
32.9019 | 600.146 | 44.1478 | 121.614 | 55.3433 | 49.348 | 75.3822 | 21.3172 | 100.442 | 25.1138 | 127.944 | 27.8747 | 187.094 | 12.1253 | 216.507 | 21.3384 | 273.317 | 22.0276
|  | 44.1478 | 157.141 | 55.1775 | 62.5093 | 74.1114 | 24.8162 | 98.552 | 29.178 | 125.536 | 33.0027 | 182.11 | 14.3559 | 213.07 | 24.7916 | 266.569 | 26.0799
|  | 44.1478 | 198.261 | 55.1775 | 81.9006 | 73.1542 | 29.0623 | 97.3764 | 33.5981 | 123.667 | 38.7648 | 178.326 | 16.6295 | 209.269 | 29.4986 | 262.075 | 29.7339
|  | 44.1478 | 274.08 | 55.1775 | 111.103 | 72.065 | 34.3746 | 95.8307 | 39.8978 | 122.07 | 45.6688 | 174.445 | 19.2823 | 204.92 | 36.1968 | 257.657 | 34.7178
|  | 44.1478 | 356.969 | 55.1775 | 143.987 | 71.1342 | 41.3504 | 94.5929 | 46.8172 | 120.372 | 55.5401 | 170.138 | 23.2877 | 201.063 | 44.0645 | 253.567 | 39.3077
|  | 44.0596 | 437.592 | 55.1775 | 187.907 | 70.356 | 50.2882 | 93.3711 | 56.0946 | 119.056 | 65.7576 | 167.437 | 27.7091 | 197.673 | 54.0703 | 249.792 | 45.3974
|  | 44.0156 | 541.779 | 55.1775 | 253.645 | 69.5167 | 61.2797 | 92.627 | 65.9539 | 117.518 | 81.8193 | 164.615 | 33.233 | 195.12 | 63.5107 | 246.073 | 54.5017
|  | 43.9716 | 600.146 | 55.1775 | 345.457 | 68.9627 | 73.9354 | 91.7971 | 77.3153 | 116.116 | 103.229 | 162.326 | 40.0168 | 192.793 | 74.3035 | 242.894 | 63.637
|  |  |  | 55.1775 | 466.778 | 68.2765 | 90.9044 | 91.0656 | 91.9945 | 115.075 | 126.796 | 160.39 | 47.097 | 190.683 | 87.1898 | 239.517 | 76.3992
|  |  |  | 55.1775 | 566.546 | 67.8002 | 113.671 | 90.5208 | 108.702 | 113.476 | 168.122 | 158.476 | 56.3739 | 188.22 | 102.514 | 236.187 | 91.6296
|  |  |  | 55.1223 | 600.146 | 67.3946 | 140.595 | 90.0693 | 131.543 | 112.684 | 205.072 | 156.429 | 67.7467 | 186.721 | 118.044 | 232.671 | 113.784
[6 empty] | 66.9914 | 180.228 | 89.7098 | 152.982 | 112.122 | 254.908 | 154.718 | 80.3693 | 185.048 | 137.011 | 229.666 | 135.926
[6 empty] | 66.724 | 228.523 | 88.8171 | 188.093 | 111.563 | 314.348 | 152.262 | 103.024 | 183.573 | 161.252 | 227.153 | 161.733
[6 empty] | 66.4576 | 295.279 | 88.551 | 239.207 | 111.117 | 384.962 | 150.295 | 130.631 | 181.746 | 191.677 | 224.443 | 196.692
[6 empty] | 66.2585 | 365.582 | 88.1093 | 309.699 | 110.453 | 487.148 | 148.206 | 168.959 | 180.298 | 226.714 | 222.21 | 237.314
[6 empty] | 66.1923 | 452.174 | 88.0213 | 415.975 | 110.232 | 569.933 | 146.731 | 205.684 | 178.861 | 269.223 | 220.439 | 280.971
[6 empty] | 66.0601 | 540.166 | 88.0213 | 527.965 | 110.012 | 600.146 | 145.416 | 269.223 | 177.969 | 311.241 | 218.683 | 330.684
[6 empty] | 66.0601 | 600.146 | 88.0213 | 573.34 |  |  | 144.402 | 324.501 | 176.905 | 372.177 | 216.94 | 414.326
[8 empty] | 88.0213 | 600.146 |  |  | 143.538 | 405.772 | 175.846 | 451.725 | 215.858 | 496.923
[12 empty] | 142.965 | 501.884 | 175.144 | 532.178 | 215.642 | 566.546
[12 empty] | 142.537 | 572.202 | 174.445 | 573.34 | 215.211 | 600.146
[12 empty] | 142.537 | 600.146 | 173.922 | 600.146