## 119_165
S&C Power Fuses - Type SMD-50 (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-50 (69 kV)
Slow Speed (TCC 119-1-6-5) | [9 empty] | Slow Speed (TCC 119-1-6-5)
Total Clearing Time-Current Characteristic Curves Dated January 25, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 25, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
4297.42 | 0.025899 | 4297.42 | 0.02621 | 4297.42 | 0.026498 | 4297.42 | 0.027408 | 4297.42 | 0.029704 | 4297.42 | 0.032386 | 4297.42 | 0.035485 | 4297.42 | 0.043112 | 4297.42 | 0.054991
3884.56 | 0.027299 | 4153.75 | 0.026709 | 2924.12 | 0.032905 | 3390.58 | 0.031591 | 4284.54 | 0.029793 | 3611.07 | 0.037515 | 4263.17 | 0.035804 | 4241.91 | 0.043803 | 4149.6 | 0.057619
2452.2 | 0.034409 | 2726.42 | 0.033498 | 1494.75 | 0.04989 | 1960.06 | 0.045805 | 2854.78 | 0.040618 | 3532.49 | 0.038192 | 4112.42 | 0.036997 | 3982.9 | 0.04691 | 3830.55 | 0.064081
1023.2 | 0.055817 | 1295.57 | 0.052119 | 1456.39 | 0.050891 | 1921.24 | 0.046493 | 2778.72 | 0.041515 | 3421.24 | 0.039308 | 3955.12 | 0.038382 | 3709.91 | 0.050993 | 3582.3 | 0.070423
969.419 | 0.057791 | 1233.62 | 0.053802 | 1374.32 | 0.053007 | 1844.06 | 0.047994 | 2653.79 | 0.043112 | 3260.89 | 0.040982 | 3739.71 | 0.040497 | 3469.47 | 0.05532 | 3313.49 | 0.078632
885.978 | 0.061402 | 1144.47 | 0.056824 | 1294.28 | 0.055485 | 1762.91 | 0.049791 | 2514.28 | 0.045083 | 3074.05 | 0.043284 | 3543.11 | 0.042686 | 3234.91 | 0.060373 | 3098.75 | 0.08693
820.315 | 0.064914 | 1060.71 | 0.060074 | 1191.18 | 0.059186 | 1668.57 | 0.052119 | 2377.34 | 0.047379 | 2912.45 | 0.045578 | 3360.2 | 0.045083 | 2971.29 | 0.067211 | 2877.71 | 0.096871
765.619 | 0.068287 | 975.253 | 0.064272 | 1100.7 | 0.063071 | 1560.43 | 0.054991 | 2225.5 | 0.050388 | 2737.35 | 0.048377 | 3174.02 | 0.047804 | 2742.83 | 0.074896 | 2565.08 | 0.11561
701.121 | 0.073132 | 886.865 | 0.069519 | 974.278 | 0.070283 | 1453.48 | 0.058601 | 2070.89 | 0.053909 | 2567.64 | 0.051707 | 3010.17 | 0.05079 | 2547.18 | 0.082718 | 2363.12 | 0.13167
634.397 | 0.079496 | 807.294 | 0.075419 | 853.794 | 0.079338 | 1349.8 | 0.062821 | 1944.44 | 0.057505 | 2403.64 | 0.055375 | 2806.65 | 0.054719 | 2325.61 | 0.09412 | 2161.88 | 0.15207
572.877 | 0.087017 | 744.478 | 0.081172 | 761.8 | 0.089293 | 1267.38 | 0.066612 | 1814.79 | 0.061707 | 2241.13 | 0.059777 | 2637.92 | 0.058717 | 2121.19 | 0.10741 | 1987.69 | 0.17459
509.62 | 0.097064 | 685.864 | 0.08806 | 692.757 | 0.098815 | 1169.93 | 0.072122 | 1688.71 | 0.066414 | 2100.08 | 0.064272 | 2410.86 | 0.065302 | 1942.5 | 0.12307 | 1825.71 | 0.20124
456.989 | 0.1087 | 637.577 | 0.094777 | 624.952 | 0.11121 | 1085.39 | 0.077778 | 1557.31 | 0.072697 | 1936.68 | 0.070703 | 2218.83 | 0.072409 | 1773.52 | 0.14158 | 1715.95 | 0.22381
412.26 | 0.12162 | 586.206 | 0.10385 | 560.971 | 0.1268 | 983.087 | 0.0865 | 1433.27 | 0.079733 | 1785.98 | 0.07801 | 2075.03 | 0.078867 | 1627.37 | 0.16157 | 1568.25 | 0.26132
362.001 | 0.14172 | 535.75 | 0.11503 | 507.585 | 0.14427 | 892.202 | 0.096871 | 1316.47 | 0.088323 | 1661.91 | 0.08556 | 1898.33 | 0.088587 | 1503.75 | 0.18385 | 1478.4 | 0.29005
330.182 | 0.15918 | 496.54 | 0.12579 | 474.215 | 0.15808 | 793.685 | 0.11144 | 1209.19 | 0.098228 | 1558.87 | 0.092913 | 1734.93 | 0.1003 | 1390.91 | 0.20836 | 1402.08 | 0.32002
293.136 | 0.18679 | 456.532 | 0.13934 | 440.829 | 0.17494 | 731.197 | 0.12393 | 1129.69 | 0.1072 | 1456.39 | 0.1017 | 1598.34 | 0.11255 | 1278.84 | 0.24064 | 1303.37 | 0.36558
253.821 | 0.22852 | 416.82 | 0.1573 | 400.075 | 0.20104 | 673.628 | 0.13879 | 1038.67 | 0.12017 | 1359.28 | 0.11155 | 1466.62 | 0.12755 | 1179.33 | 0.27599 | 1217.68 | 0.41598
221.544 | 0.28097 | 379.802 | 0.17898 | 363.816 | 0.23149 | 615.647 | 0.15667 | 967.482 | 0.13246 | 1256.02 | 0.12455 | 1383.97 | 0.13976 | 1094.11 | 0.31372 | 1129.69 | 0.48042
199.86 | 0.33003 | 345.035 | 0.20426 | 334.168 | 0.26419 | 554.834 | 0.18203 | 901.169 | 0.14659 | 1161.77 | 0.14004 | 1296.87 | 0.15405 | 1021.16 | 0.35414 | 1054.37 | 0.54719
178.504 | 0.39858 | 315.968 | 0.23288 | 305.405 | 0.30482 | 506.571 | 0.20877 | 838.563 | 0.16286 | 1079.98 | 0.1559 | 1218.9 | 0.17014 | 952.125 | 0.40097 | 969.419 | 0.64464
162.977 | 0.46401 | 290.8 | 0.26419 | 280.798 | 0.35064 | 450.185 | 0.25039 | 772.541 | 0.18403 | 1007.97 | 0.1739 | 1144.47 | 0.18791 | 888.64 | 0.45398 | 915.705 | 0.72625
150.145 | 0.5343 | 266.302 | 0.30451 | 258.431 | 0.40216 | 406.122 | 0.29587 | 721.752 | 0.20507 | 926.76 | 0.19826 | 1068.16 | 0.21023 | 824.427 | 0.51758 | 854.649 | 0.83627
139.714 | 0.60855 | 247.306 | 0.34272 | 238.8 | 0.46079 | 379.422 | 0.332 | 668.261 | 0.23242 | 817.04 | 0.24304 | 984.07 | 0.24112 | 765.619 | 0.59599 | 803.267 | 0.95249
121.218 | 0.78476 | 226.926 | 0.39504 | 224.219 | 0.51553 | 340.238 | 0.39898 | 623.08 | 0.26002 | 734.862 | 0.29062 | 923.984 | 0.26842 | 723.197 | 0.66019 | 743.734 | 1.1232
107.833 | 0.97547 | 207.601 | 0.45896 | 210.528 | 0.57391 | 309.092 | 0.47238 | 575.748 | 0.29587 | 668.261 | 0.34136 | 860.652 | 0.30331 | 675.652 | 0.74822 | 698.322 | 1.2793
97.4738 | 1.1804 | 189.164 | 0.53802 | 196.884 | 0.644 | 288.195 | 0.53483 | 541.134 | 0.32872 | 605.269 | 0.40537 | 803.267 | 0.34204 | 622.457 | 0.87537 | 649.808 | 1.4864
89.2623 | 1.4087 | 165.771 | 0.68832 | 178.861 | 0.7678 | 270.327 | 0.59717 | 502.534 | 0.37292 | 549.313 | 0.48329 | 749.708 | 0.38726 | 583.282 | 0.98815 | 610.131 | 1.6997
81.3349 | 1.6946 | 148.354 | 0.84044 | 166.435 | 0.87798 | 254.838 | 0.66085 | 465.755 | 0.42601 | 500.528 | 0.57163 | 702.525 | 0.43499 | 550.963 | 1.1055 | 577.478 | 1.9149
75.1564 | 1.9984 | 134.639 | 1.009 | 155.805 | 1 | 236.424 | 0.75644 | 429.944 | 0.49152 | 460.199 | 0.66217 | 640.133 | 0.51655 | 516.288 | 1.2542 | 551.515 | 2.1338
70.2154 | 2.3195 | 122.192 | 1.221 | 145.416 | 1.1469 | 222.21 | 0.85136 | 398.08 | 0.56318 | 420.589 | 0.77855 | 582.117 | 0.61953 | 491.107 | 1.3865 | 527.246 | 2.3567
66.2585 | 2.6577 | 110.784 | 1.4938 | 134.101 | 1.3539 | 206.153 | 0.9813 | 368.208 | 0.64592 | 387.475 | 0.90724 | 532.012 | 0.73789 | 468.558 | 1.5298 | 498.032 | 2.6976
62.3998 | 3.0542 | 99.9415 | 1.8623 | 124.785 | 1.5714 | 194.341 | 1.1 | 325.591 | 0.81252 | 362.001 | 1.0313 | 497.534 | 0.84294 | 444.37 | 1.7167 | 470.907 | 3.0786
59.1194 | 3.4891 | 93.4645 | 2.1509 | 114.731 | 1.8903 | 183.023 | 1.2381 | 297.566 | 0.962 | 337.864 | 1.1804 | 468.09 | 0.95249 | 420.168 | 1.9494 | 446.151 | 3.4891
55.6764 | 4.0336 | 87.3199 | 2.5114 | 108.482 | 2.136 | 173.749 | 1.3783 | 272.226 | 1.1435 | 314.392 | 1.362 | 437.754 | 1.0968 | 399.276 | 2.1962 | 425.666 | 3.9464
52.1202 | 4.8185 | 82.1523 | 2.8947 | 103.088 | 2.3755 | 164.121 | 1.5497 | 252.303 | 1.3286 | 292.843 | 1.5761 | 414.741 | 1.2295 | 381.706 | 2.4498 | 408.975 | 4.389
49.1339 | 5.6993 | 77.2133 | 3.3598 | 98.3551 | 2.6236 | 155.493 | 1.7372 | 235.244 | 1.5329 | 276.064 | 1.7827 | 394.908 | 1.362 | 362.726 | 2.7737 | 393.331 | 4.9006
46.3651 | 6.6944 | 73.7418 | 3.7852 | 93.2777 | 2.9734 | 147.91 | 1.934 | 222.655 | 1.7235 | 257.657 | 2.0671 | 372.653 | 1.5497 | 344.001 | 3.1843 | 377.908 | 5.4991
44.1478 | 7.7778 | 69.6559 | 4.4108 | 89.2623 | 3.3299 | 139.714 | 2.1984 | 209.269 | 1.9689 | 242.894 | 2.3684 | 355.188 | 1.7252 | 328.535 | 3.6018 | 363.816 | 6.1158
42.2051 | 8.8939 | 66.0601 | 5.0942 | 85.0787 | 3.7702 | 132.369 | 2.4965 | 196.687 | 2.247 | 229.666 | 2.6949 | 335.172 | 1.9669 | 313.137 | 4.1146 | 351.653 | 6.7747
40.6313 | 10.2209 | 62.5247 | 5.9717 | 81.8244 | 4.2013 | 126.671 | 2.7764 | 183.023 | 2.6577 | 219.559 | 3.015 | 322.351 | 2.153 | 299.058 | 4.7426 | 337.864 | 7.6475
39.3123 | 11.7927 | 59.5347 | 7.0074 | 78.3803 | 4.7191 | 120.372 | 3.1529 | 174.271 | 2.9764 | 207.601 | 3.4787 | 310.021 | 2.3637 | 287.906 | 5.3112 | 328.535 | 8.4967
37.8086 | 14.3987 | 56.9149 | 8.2145 | 75.5331 | 5.3059 | 114.731 | 3.5661 | 164.286 | 3.4272 | 197.871 | 3.9308 | 300.257 | 2.5694 | 278.282 | 5.9599 | 319.782 | 9.4683
36.6544 | 17.6683 | 54.5738 | 9.62 | 73.3006 | 5.9186 | 110.012 | 3.9898 | 155.028 | 3.9779 | 189.732 | 4.4196 | 287.331 | 2.8491 | 267.637 | 6.8017 | 313.45 | 10.3435
35.6423 | 21.8315 | 52.5914 | 11.2771 | 70.5673 | 6.8764 | 105.171 | 4.5307 | 148.949 | 4.4504 | 183.206 | 4.9055 | 278.56 | 3.0939 | 259.467 | 7.7009 | 304.795 | 11.8161
35.0064 | 26.0023 | 50.8841 | 13.3385 | 68.1401 | 7.9496 | 101.148 | 5.0841 | 144.113 | 4.8715 | 178.147 | 5.3483 | 268.173 | 3.4204 | 251.295 | 8.9382 | 298.759 | 13.1673
34.3132 | 32.6441 | 49.6277 | 15.5433 | 65.6649 | 9.3468 | 97.3764 | 5.6993 | 138.601 | 5.407 | 171.504 | 6.0015 | 258.173 | 3.7965 | 244.112 | 10.2006 | 291.966 | 14.7902
33.8024 | 39.3467 | 48.354 | 18.6234 | 63.5332 | 10.9351 | 94.027 | 6.4145 | 133.433 | 5.9955 | 165.937 | 6.7077 | 249.792 | 4.168 | 239.278 | 11.4692 | 285.327 | 16.8791
33.4325 | 48.4735 | 47.5389 | 21.6803 | 62.0265 | 12.4796 | 90.9746 | 7.1979 | 128.2 | 6.8017 | 161.678 | 7.4156 | 240.718 | 4.6678 | 233.603 | 12.9597 | 279.677 | 19.0727
33.1993 | 60.1339 | 46.9718 | 25.3142 | 60.5555 | 14.4848 | 88.2857 | 8.093 | 123.543 | 7.7546 | 156.899 | 8.371 | 233.137 | 5.1502 | 229.666 | 14.5136 | 273.317 | 22.0495
33.0668 | 79.0235 | 46.3187 | 29.7339 | 59.4157 | 16.8289 | 85.8479 | 9.1812 | 119.772 | 8.7277 | 151.806 | 9.4777 | 226.246 | 5.6824 | 225.568 | 16.2216 | 266.569 | 26.0799
33.0007 | 108.271 | 45.812 | 34.7523 | 58.5311 | 19.4168 | 83.8959 | 10.395 | 115.768 | 10.2209 | 147.762 | 10.8486 | 219.779 | 6.2509 | 221.766 | 18.1847 | 262.075 | 29.7339
33.0007 | 153.286 | 45.3108 | 40.9416 | 57.6596 | 23.2877 | 81.5792 | 12.1012 | 112.234 | 11.8632 | 143.825 | 12.4425 | 212.219 | 7.1197 | 216.507 | 21.3596 | 257.657 | 34.7523
33.0007 | 221.153 | 44.9048 | 48.5699 | 56.9149 | 27.6541 | 79.6445 | 14.0316 | 109.135 | 13.6875 | 140.555 | 14.2423 | 204.715 | 8.1091 | 213.07 | 24.7916 | 253.567 | 39.3077
33.0007 | 317.486 | 44.547 | 58.7173 | 56.2922 | 33.3985 | 77.9114 | 16.0613 | 106.44 | 16.0294 | 136.947 | 16.7455 | 198.466 | 9.2361 | 209.269 | 29.4986 | 249.792 | 45.3974
32.9677 | 467.707 | 44.3691 | 72.553 | 55.7321 | 40.1363 | 76.8282 | 18.1306 | 104.541 | 18.3298 | 133.967 | 19.4361 | 192.215 | 10.6352 | 204.92 | 36.1968 | 246.073 | 54.5017
32.9348 | 545.559 | 44.1478 | 91.6296 | 55.3433 | 49.3971 | 75.3822 | 21.3384 | 102.471 | 21.4234 | 130.268 | 23.5435 | 187.094 | 12.1373 | 201.063 | 44.0645 | 242.894 | 63.637
32.9019 | 600.146 | 44.1478 | 121.614 | 55.1775 | 62.5093 | 74.1114 | 24.8409 | 100.442 | 25.1388 | 127.944 | 27.8747 | 182.11 | 14.3702 | 197.673 | 54.0703 | 239.517 | 76.3992
|  | 44.1478 | 157.141 | 55.1775 | 81.9006 | 73.1542 | 29.0623 | 98.552 | 29.178 | 125.536 | 33.0355 | 178.326 | 16.6295 | 195.12 | 63.5107 | 236.187 | 91.6296
|  | 44.1478 | 198.261 | 55.1775 | 111.103 | 72.065 | 34.4088 | 97.3764 | 33.6315 | 123.667 | 38.7648 | 174.445 | 19.3014 | 192.793 | 74.3035 | 232.671 | 113.784
|  | 44.1478 | 274.08 | 55.1775 | 143.987 | 71.1342 | 41.3914 | 95.8307 | 39.9374 | 122.07 | 45.6688 | 170.138 | 23.2877 | 190.683 | 87.1898 | 229.666 | 135.926
|  | 44.1478 | 356.969 | 55.1775 | 187.907 | 70.356 | 50.3382 | 94.5929 | 46.8172 | 120.372 | 55.5401 | 167.437 | 27.7366 | 188.22 | 102.616 | 227.153 | 161.733
|  | 44.0596 | 437.592 | 55.1775 | 253.645 | 69.5167 | 61.3406 | 93.3711 | 56.0946 | 119.056 | 65.7576 | 164.615 | 33.266 | 186.721 | 118.044 | 224.443 | 196.692
|  | 44.0156 | 541.779 | 55.1775 | 345.457 | 68.9627 | 73.9354 | 92.627 | 65.9539 | 117.518 | 81.8193 | 162.326 | 40.0168 | 185.048 | 137.011 | 222.21 | 237.314
|  | 43.9716 | 600.146 | 55.1775 | 466.778 | 68.2765 | 90.9044 | 91.7971 | 77.3153 | 116.116 | 103.229 | 160.39 | 47.097 | 183.573 | 161.252 | 220.439 | 280.971
|  |  |  | 55.1775 | 566.546 | 67.8002 | 113.671 | 91.0656 | 91.9945 | 115.075 | 126.796 | 158.476 | 56.3739 | 181.746 | 191.677 | 218.683 | 330.684
|  |  |  | 55.1223 | 600.146 | 67.3946 | 140.735 | 90.5208 | 108.702 | 113.476 | 168.122 | 156.429 | 67.7467 | 180.298 | 226.714 | 216.94 | 414.326
[6 empty] | 66.9914 | 180.228 | 90.0693 | 131.543 | 112.684 | 205.072 | 154.718 | 80.3693 | 178.861 | 269.223 | 215.858 | 496.923
[6 empty] | 66.724 | 228.523 | 89.7098 | 152.982 | 112.122 | 254.908 | 152.262 | 103.024 | 177.969 | 311.55 | 215.642 | 566.546
[6 empty] | 66.4576 | 295.279 | 88.8171 | 188.093 | 111.563 | 314.348 | 150.295 | 130.631 | 176.905 | 372.177 | 215.211 | 600.146
[6 empty] | 66.2585 | 365.582 | 88.551 | 239.207 | 111.117 | 384.962 | 148.206 | 168.959 | 175.846 | 451.725
[6 empty] | 66.1923 | 452.174 | 88.1093 | 310.007 | 110.453 | 487.148 | 146.731 | 205.684 | 175.144 | 532.178
[6 empty] | 66.0601 | 540.166 | 88.0213 | 415.975 | 110.232 | 569.933 | 145.416 | 269.223 | 174.445 | 573.91
[6 empty] | 66.0601 | 600.146 | 88.0213 | 527.965 | 110.012 | 600.146 | 144.402 | 324.501 | 173.922 | 600.146
[8 empty] | 88.0213 | 573.91 |  |  | 143.538 | 405.772
[8 empty] | 88.0213 | 600.146 |  |  | 142.965 | 501.884
[12 empty] | 142.537 | 572.202
[12 empty] | 142.537 | 600.146