## 119_19B
S&C Power Fuses - Types SMD-1A (15E thru 100E) and SMD-2B (15E thru 250E) (115 and 138 kV) | [9 empty] | S&C Power Fuses - Types SMD-1A (15E thru 100E) and SMD-2B (15E thru 250E) (115 and 138 kV) | [9 empty] | S&C Power Fuses - Types SMD-1A (15E thru 100E) and SMD-2B (15E thru 250E) (115 and 138 kV)
Slow Speed (TCC 119-1-9) | [9 empty] | Slow Speed (TCC 119-1-9) | [9 empty] | Slow Speed (TCC 119-1-9)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
9995.88 | 0.051397 | 9995.88 | 0.0515 | 9995.88 | 0.051603 | 9995.88 | 0.051707 | 9995.88 | 0.052226 | 9995.88 | 0.052593 | 9995.88 | 0.053228 | 9995.88 | 0.05463 | 9995.88 | 0.056803 | 10027.7 | 0.060058 | 10027.7 | 0.064997 | 10027.7 | 0.068201 | 10027.7 | 0.072761 | 10027.7 | 0.086056
8175.75 | 0.053388 | 8450.05 | 0.053228 | 7215.08 | 0.054904 | 7684.25 | 0.054521 | 7143.29 | 0.056182 | 7902.45 | 0.055734 | 7200.66 | 0.058183 | 7164.75 | 0.060983 | 7382.95 | 0.064302 | 9124.51 | 0.062802 | 9166.36 | 0.068632 | 9245.36 | 0.071603 | 8994.93 | 0.079607 | 8989.79 | 0.095237
6740.76 | 0.055401 | 7015.86 | 0.055124 | 5784.45 | 0.057374 | 6253.7 | 0.05686 | 5715.45 | 0.059418 | 6469.98 | 0.058709 | 5767.12 | 0.062401 | 5732.62 | 0.066792 | 7265.76 | 0.064754 | 8091.58 | 0.066694 | 8027.03 | 0.074404 | 7751.74 | 0.081592 | 7935.71 | 0.088759 | 7787.3 | 0.11072
5313.09 | 0.058008 | 5585.49 | 0.057661 | 4354.34 | 0.060983 | 4821.92 | 0.060315 | 4285.22 | 0.064431 | 5043.87 | 0.063345 | 4336.96 | 0.069797 | 5524.39 | 0.06787 | 6980.86 | 0.065996 | 7089.9 | 0.071726 | 6905.75 | 0.082721 | 6711.02 | 0.092549 | 6913.66 | 0.10143 | 6854.58 | 0.12879
3885.19 | 0.061719 | 4154.42 | 0.061288 | 2924.64 | 0.066859 | 3391.16 | 0.065864 | 2855.29 | 0.074634 | 3611.68 | 0.071923 | 4263.85 | 0.070428 | 5286.59 | 0.069518 | 6640.4 | 0.067666 | 6194.47 | 0.07834 | 6120.5 | 0.091652 | 5954.71 | 0.10468 | 6071.67 | 0.11698 | 6050.87 | 0.15128
2452.66 | 0.068074 | 2726.92 | 0.067396 | 1495.07 | 0.082731 | 1960.45 | 0.079169 | 2779.23 | 0.075459 | 3533.09 | 0.0725 | 4113.08 | 0.071635 | 5038.83 | 0.071136 | 6335.53 | 0.069379 | 5329.18 | 0.087848 | 5381.26 | 0.10444 | 5295.75 | 0.11983 | 5250.5 | 0.13939 | 5433.85 | 0.17558
1023.44 | 0.087846 | 1295.86 | 0.084655 | 1456.7 | 0.083646 | 1921.63 | 0.079805 | 2654.28 | 0.076906 | 3421.82 | 0.073596 | 3955.76 | 0.072937 | 4788.29 | 0.073009 | 5848.43 | 0.072645 | 4725.9 | 0.097556 | 4804.96 | 0.11826 | 4535.19 | 0.1441 | 4548.18 | 0.16781 | 4854.69 | 0.20778
969.646 | 0.0898 | 1233.89 | 0.086366 | 1374.61 | 0.085592 | 1844.43 | 0.081336 | 2514.75 | 0.078853 | 3261.45 | 0.075158 | 3740.33 | 0.075008 | 4500.43 | 0.075535 | 5496.84 | 0.075459 | 4167 | 0.11066 | 4357.16 | 0.13284 | 3879.42 | 0.17689 | 3919.57 | 0.20647 | 4349.69 | 0.24616
886.19 | 0.093279 | 1144.73 | 0.089085 | 1294.56 | 0.087934 | 1763.27 | 0.082896 | 2377.79 | 0.081092 | 3074.59 | 0.077369 | 3543.71 | 0.07706 | 4242.59 | 0.078382 | 5171.55 | 0.078382 | 3697.4 | 0.12581 | 3951.09 | 0.14999 | 3375.92 | 0.21615 | 3406.96 | 0.25535 | 3910.62 | 0.29315
820.514 | 0.096601 | 1060.96 | 0.092258 | 1191.45 | 0.091615 | 1668.91 | 0.085165 | 2225.93 | 0.083981 | 2912.97 | 0.079566 | 3360.78 | 0.079407 | 3983.55 | 0.081499 | 4831.58 | 0.082071 | 3155.54 | 0.15215 | 3454.06 | 0.17964 | 3010.93 | 0.25623 | 3035.14 | 0.30637 | 3546.17 | 0.34474
765.808 | 0.10004 | 975.481 | 0.096312 | 1100.95 | 0.095449 | 1560.76 | 0.087846 | 2071.29 | 0.087321 | 2737.85 | 0.0824 | 3174.57 | 0.081989 | 3710.52 | 0.085506 | 4554.76 | 0.085763 | 2747.56 | 0.18318 | 3071.82 | 0.2121 | 2738.15 | 0.29874 | 2733.45 | 0.36527 | 3199.17 | 0.41054
701.297 | 0.10465 | 887.076 | 0.10135 | 974.506 | 0.10227 | 1453.79 | 0.09134 | 1944.83 | 0.090794 | 2568.12 | 0.085506 | 3010.7 | 0.08491 | 3470.06 | 0.089531 | 4150.27 | 0.092166 | 2471.63 | 0.21332 | 2685.4 | 0.25963 | 2470.21 | 0.35313 | 2433.74 | 0.44507 | 2914.33 | 0.48611
634.559 | 0.1109 | 807.49 | 0.10719 | 854 | 0.11112 | 1350.09 | 0.095449 | 1815.16 | 0.094878 | 2404.09 | 0.089085 | 2807.16 | 0.088641 | 3235.47 | 0.094594 | 3831.18 | 0.098651 | 2166.89 | 0.25963 | 2319.55 | 0.3293 | 2246.42 | 0.41622 | 2196.85 | 0.53398 | 2621.64 | 0.58859
573.026 | 0.11834 | 744.662 | 0.11291 | 761.988 | 0.12086 | 1267.66 | 0.099146 | 1689.06 | 0.099543 | 2241.56 | 0.093372 | 2638.4 | 0.092628 | 2971.82 | 0.10125 | 3582.9 | 0.10465 | 1911.73 | 0.31817 | 2020.81 | 0.41337 | 2080.64 | 0.47646 | 1972.83 | 0.64804 | 2393.7 | 0.69933
509.755 | 0.12846 | 686.037 | 0.11953 | 692.931 | 0.1304 | 1170.2 | 0.10433 | 1557.64 | 0.10549 | 2100.49 | 0.097865 | 2411.32 | 0.099047 | 2743.33 | 0.10892 | 3314.06 | 0.1128 | 1682.75 | 0.39621 | 1808.53 | 0.50253 | 1906.26 | 0.55519 | 1776.74 | 0.79279 | 2195.59 | 0.82712
457.113 | 0.13999 | 637.74 | 0.12629 | 625.112 | 0.14268 | 1085.64 | 0.11001 | 1433.58 | 0.11257 | 1937.06 | 0.10392 | 2219.26 | 0.10591 | 2547.65 | 0.11658 | 3099.29 | 0.12098 | 1528.55 | 0.46861 | 1657.9 | 0.58389 | 1731.58 | 0.66382 | 1614.84 | 0.95063 | 1988.7 | 1.0009
412.374 | 0.15302 | 586.358 | 0.13531 | 561.118 | 0.15832 | 983.316 | 0.11858 | 1316.76 | 0.12086 | 1786.35 | 0.11123 | 2075.44 | 0.11246 | 2326.05 | 0.12769 | 2878.22 | 0.13092 | 1371.89 | 0.57066 | 1499.1 | 0.70618 | 1618.54 | 0.75339 | 1450.18 | 1.1811 | 1799.24 | 1.2224
362.104 | 0.17305 | 535.891 | 0.14644 | 507.721 | 0.17567 | 892.415 | 0.12884 | 1209.46 | 0.13066 | 1662.25 | 0.11858 | 1898.71 | 0.12183 | 2121.6 | 0.14083 | 2565.55 | 0.14954 | 1224.27 | 0.70698 | 1366.41 | 0.84774 | 1512.89 | 0.858 | 1288.96 | 1.4997 | 1706.99 | 1.359
330.277 | 0.19068 | 496.673 | 0.15721 | 474.343 | 0.18935 | 793.879 | 0.14311 | 1129.95 | 0.13943 | 1559.2 | 0.12579 | 1735.29 | 0.13343 | 1942.88 | 0.15643 | 2363.57 | 0.16527 | 1091.28 | 0.88495 | 1256.2 | 1.0032 | 1407.67 | 0.99065 | 1164.83 | 1.874 | 1531.17 | 1.708
293.222 | 0.21824 | 456.656 | 0.17065 | 440.95 | 0.20635 | 731.378 | 0.15565 | 1038.91 | 0.15226 | 1456.7 | 0.1345 | 1598.67 | 0.14556 | 1773.89 | 0.17479 | 2162.3 | 0.18541 | 980.568 | 1.0932 | 1121.02 | 1.2709 | 1302.3 | 1.163 | 1047.25 | 2.3864 | 1375.82 | 2.1675
253.898 | 0.26076 | 416.935 | 0.18859 | 400.187 | 0.23243 | 673.798 | 0.17031 | 967.708 | 0.16445 | 1359.57 | 0.14426 | 1466.93 | 0.16023 | 1627.71 | 0.19453 | 1988.09 | 0.20801 | 878.565 | 1.3755 | 1030.6 | 1.5153 | 1139.78 | 1.5318 | 963.331 | 2.9011 | 1242.62 | 2.7396
221.613 | 0.31375 | 379.909 | 0.21031 | 363.919 | 0.26285 | 615.805 | 0.18822 | 901.384 | 0.1785 | 1256.3 | 0.1569 | 1384.27 | 0.17236 | 1504.07 | 0.21672 | 1826.08 | 0.23453 | 793.957 | 1.7011 | 955.1 | 1.787 | 1013.07 | 1.9856 | 882.091 | 3.6272 | 1126.81 | 3.4707
199.923 | 0.36307 | 345.133 | 0.23571 | 334.264 | 0.29548 | 554.979 | 0.21349 | 838.765 | 0.19473 | 1162.03 | 0.17236 | 1297.15 | 0.18653 | 1391.21 | 0.24119 | 1716.3 | 0.25688 | 718.73 | 2.1269 | 894.797 | 2.0609 | 892.752 | 2.6486 | 823.095 | 4.3643 | 1027.66 | 4.4374
178.561 | 0.43207 | 316.06 | 0.26443 | 305.494 | 0.3365 | 506.706 | 0.24023 | 772.731 | 0.21564 | 1080.23 | 0.18803 | 1219.17 | 0.20267 | 1279.12 | 0.27303 | 1568.58 | 0.2943 | 653.241 | 2.6684 | 824.981 | 2.4854 | 800.342 | 3.4747 | 760.177 | 5.5481 | 954.007 | 5.5354
163.029 | 0.4975 | 290.886 | 0.29577 | 280.881 | 0.38283 | 450.308 | 0.28163 | 721.932 | 0.23665 | 1008.2 | 0.20615 | 1144.73 | 0.22021 | 1179.6 | 0.30815 | 1478.71 | 0.32298 | 588.646 | 3.4292 | 763.227 | 3.0025 | 715.857 | 4.6909 | 698.862 | 7.4175 | 882.595 | 7.1628
150.194 | 0.56884 | 266.382 | 0.33616 | 258.509 | 0.43424 | 406.235 | 0.32753 | 668.43 | 0.26391 | 926.979 | 0.23012 | 1068.41 | 0.2424 | 1094.36 | 0.34605 | 1402.38 | 0.35269 | 535.929 | 4.4045 | 707.713 | 3.6168 | 646.549 | 6.3583 | 655.112 | 9.5161 | 821.683 | 9.3808
139.76 | 0.64329 | 247.381 | 0.37488 | 238.873 | 0.49304 | 379.529 | 0.36343 | 623.24 | 0.29137 | 817.238 | 0.27495 | 984.3 | 0.27331 | 1021.4 | 0.38629 | 1303.65 | 0.39806 | 488.772 | 5.7027 | 658.494 | 4.332 | 586.294 | 8.7577 | 619.394 | 12.1109 | 776.883 | 12.1318
121.259 | 0.82024 | 226.996 | 0.42735 | 224.288 | 0.54763 | 340.335 | 0.43078 | 575.898 | 0.32753 | 735.044 | 0.32233 | 924.202 | 0.30024 | 952.348 | 0.43294 | 1217.95 | 0.44881 | 442.207 | 7.7209 | 613.399 | 5.2723 | 551.481 | 11.1458 | 584.953 | 16.7962 | 737.895 | 15.6806
107.87 | 1.0119 | 207.666 | 0.49156 | 210.594 | 0.60704 | 309.182 | 0.50401 | 541.277 | 0.36018 | 668.43 | 0.37263 | 860.859 | 0.33515 | 888.852 | 0.4857 | 1129.95 | 0.51265 | 409.106 | 10.1291 | 567.159 | 6.558 | 518.142 | 15.0471 | 566.834 | 21.6226 | 706.096 | 20.2095
97.5079 | 1.2188 | 189.224 | 0.57112 | 196.946 | 0.67695 | 288.28 | 0.56657 | 502.669 | 0.40407 | 605.425 | 0.43685 | 803.463 | 0.37413 | 824.627 | 0.54927 | 1054.61 | 0.57975 | 376.108 | 14.2584 | 530.135 | 8.0413 | 493.548 | 20.3839 | 545.519 | 30.1943 | 681.88 | 25.7646
89.2939 | 1.4475 | 165.825 | 0.72169 | 178.919 | 0.80159 | 270.408 | 0.62929 | 465.881 | 0.45742 | 549.457 | 0.5147 | 749.893 | 0.41888 | 765.808 | 0.62741 | 969.646 | 0.67695 | 352.362 | 19.2933 | 503.242 | 9.5817 | 475.26 | 27.2834 | 528.017 | 41.162 | 661.515 | 34.0145
81.3641 | 1.733 | 148.403 | 0.87445 | 166.489 | 0.91196 | 254.915 | 0.69339 | 430.063 | 0.52301 | 500.662 | 0.60341 | 702.701 | 0.46666 | 723.377 | 0.69201 | 915.922 | 0.75793 | 335.637 | 26.2713 | 479.082 | 11.5752 | 458.436 | 37.9902 | 514.891 | 56.8575 | 642.86 | 45.8416
75.1837 | 2.0377 | 134.684 | 1.0448 | 155.856 | 1.0334 | 236.496 | 0.78887 | 398.191 | 0.59502 | 460.324 | 0.69408 | 640.296 | 0.54817 | 675.823 | 0.77946 | 854.854 | 0.86748 | 324.126 | 35.2038 | 458.174 | 13.9834 | 445.763 | 51.9679 | 506.419 | 75.4514 | 627.598 | 62.708
70.2411 | 2.3581 | 122.233 | 1.2571 | 145.464 | 1.1816 | 222.278 | 0.88412 | 368.312 | 0.67695 | 420.705 | 0.81045 | 582.268 | 0.6504 | 622.617 | 0.90741 | 803.463 | 0.98397 | 314.806 | 49.7828 | 439.433 | 17.4933 | 435.678 | 75.8414 | 500.085 | 100.298 | 616.918 | 87.1668
66.283 | 2.6989 | 110.822 | 1.5293 | 134.146 | 1.3894 | 206.217 | 1.0139 | 325.685 | 0.84353 | 387.583 | 0.93879 | 532.153 | 0.76939 | 583.434 | 1.02 | 743.918 | 1.1547 | 307.156 | 73.7847 | 426.553 | 21.1086 | 430.476 | 101.57 | 496.664 | 130.83 | 610.598 | 121.861
62.423 | 3.0983 | 99.9763 | 1.9 | 124.827 | 1.6061 | 194.402 | 1.133 | 297.654 | 0.99287 | 362.104 | 1.0627 | 497.667 | 0.87445 | 551.108 | 1.1375 | 698.497 | 1.3111 | 302.794 | 105.664 | 413.577 | 26.4828 | 428.51 | 151.839 | 492.702 | 187.465 | 608.506 | 162.177
59.1416 | 3.5319 | 93.4974 | 2.1899 | 114.77 | 1.9268 | 183.081 | 1.2723 | 272.307 | 1.1757 | 337.961 | 1.2115 | 468.217 | 0.98397 | 516.426 | 1.2851 | 649.973 | 1.5172 | 301.067 | 145.288 | 402.375 | 33.4351 | 427.286 | 209.977 | 490.733 | 247.492 | 606.768 | 205.104
55.6974 | 4.079 | 87.3509 | 2.5494 | 108.519 | 2.1724 | 173.804 | 1.4132 | 252.379 | 1.3605 | 314.483 | 1.3935 | 437.874 | 1.1284 | 491.239 | 1.4174 | 610.288 | 1.7295 | 301.412 | 218.317 | 392.372 | 42.14 | 426.797 | 303.122 | 490.452 | 337.004 | 606.074 | 260.734
52.1401 | 4.8639 | 82.1818 | 2.9325 | 103.124 | 2.4105 | 164.175 | 1.5822 | 235.316 | 1.5649 | 292.929 | 1.6078 | 414.856 | 1.2609 | 468.685 | 1.5602 | 577.629 | 1.9481 | 302.102 | 312.643 | 385.696 | 51.5529 | 426.309 | 408.052 | 489.051 | 454.964 | 606.768 | 347.391
49.1528 | 5.7422 | 77.2413 | 3.4002 | 98.3895 | 2.6614 | 155.544 | 1.7715 | 222.723 | 1.7556 | 276.146 | 1.8146 | 395.018 | 1.3935 | 444.492 | 1.7469 | 551.66 | 2.1659 | 301.757 | 422.56 | 379.567 | 62.996 | 426.309 | 548.362 | 488.492 | 548.99 | 605.381 | 446.19
46.383 | 6.7385 | 73.7687 | 3.8223 | 93.3106 | 3.0127 | 147.958 | 1.9676 | 209.334 | 2.0034 | 257.735 | 2.0998 | 372.759 | 1.5807 | 420.284 | 1.9815 | 527.385 | 2.3865 | 301.929 | 528.928 | 374.819 | 79.261 | 426.309 | 592.445 | 487.654 | 595.506 | 605.035 | 541.186
44.1651 | 7.8213 | 69.6814 | 4.4497 | 89.2939 | 3.3698 | 139.76 | 2.2341 | 196.749 | 2.2815 | 242.968 | 2.4009 | 355.289 | 1.7556 | 399.387 | 2.2296 | 498.165 | 2.7287 | 301.757 | 590.412 | 369.92 | 99.1559 |  |  |  |  | 605.035 | 595.848
42.2217 | 8.9428 | 66.0845 | 5.1338 | 85.1091 | 3.8108 | 132.414 | 2.5316 | 183.081 | 2.6935 | 229.736 | 2.726 | 335.268 | 1.9994 | 381.813 | 2.4814 | 471.034 | 3.1107 |  |  | 366.13 | 132.262
40.6474 | 10.2763 | 62.548 | 6.0125 | 81.8537 | 4.2412 | 126.714 | 2.8118 | 174.327 | 3.0127 | 219.627 | 3.0491 | 322.445 | 2.1855 | 362.829 | 2.8034 | 446.273 | 3.5213 |  |  | 364.667 | 174.913
39.3279 | 11.8442 | 59.557 | 7.0487 | 78.4086 | 4.7628 | 120.413 | 3.1862 | 164.339 | 3.462 | 207.666 | 3.5108 | 310.111 | 2.3937 | 344.1 | 3.215 | 425.784 | 3.9783 |  |  | 364.25 | 222.992
37.8236 | 14.4521 | 56.9364 | 8.2552 | 75.5605 | 5.3486 | 114.77 | 3.6033 | 155.078 | 4.0142 | 197.933 | 3.9624 | 300.345 | 2.6009 | 328.63 | 3.6359 | 409.088 | 4.4187 |  |  | 364.458 | 280.728
36.6691 | 17.7227 | 54.5945 | 9.6682 | 73.3274 | 5.9586 | 110.049 | 4.0263 | 148.998 | 4.4855 | 189.792 | 4.4542 | 287.416 | 2.883 | 313.228 | 4.1489 | 393.441 | 4.9325 |  |  | 363.833 | 389.107
35.6566 | 21.8859 | 52.6115 | 11.3231 | 70.5932 | 6.916 | 105.207 | 4.5669 | 144.161 | 4.9079 | 183.265 | 4.9325 | 278.643 | 3.1294 | 299.146 | 4.7771 | 378.014 | 5.5281 |  |  | 364.041 | 478.757
35.0205 | 26.0455 | 50.9036 | 13.3811 | 68.1652 | 7.9872 | 101.183 | 5.1184 | 138.647 | 5.4403 | 178.204 | 5.3808 | 268.253 | 3.4516 | 287.992 | 5.3433 | 363.919 | 6.1463 |  |  | 363.625 | 574.402
34.3271 | 32.7154 | 49.6468 | 15.5933 | 65.6892 | 9.3919 | 97.4105 | 5.7365 | 133.477 | 6.0306 | 171.56 | 6.0366 | 258.251 | 3.8261 | 278.364 | 5.9885 | 351.754 | 6.8063 |  |  | 363.001 | 595.848
33.816 | 39.4032 | 48.3726 | 18.6873 | 63.5568 | 10.9774 | 94.0601 | 6.4549 | 128.243 | 6.8404 | 165.99 | 6.7385 | 249.868 | 4.2032 | 267.717 | 6.8267 | 337.961 | 7.6817
33.4461 | 48.5138 | 47.5572 | 21.7333 | 62.0496 | 12.5139 | 91.0068 | 7.2344 | 123.585 | 7.7822 | 161.73 | 7.4547 | 240.791 | 4.7013 | 259.545 | 7.7357 | 328.63 | 8.5322
33.2128 | 60.2106 | 46.99 | 25.377 | 60.5781 | 14.5246 | 88.3171 | 8.1323 | 119.813 | 8.7657 | 156.95 | 8.4052 | 233.208 | 5.1854 | 251.371 | 8.9696 | 319.875 | 9.4957
33.0802 | 79.1108 | 46.3367 | 29.7505 | 59.438 | 16.8752 | 85.8785 | 9.2151 | 115.808 | 10.266 | 151.856 | 9.5148 | 226.316 | 5.7136 | 244.186 | 10.2353 | 313.541 | 10.3796
33.0141 | 108.402 | 45.8298 | 34.808 | 58.5531 | 19.4499 | 83.9259 | 10.4212 | 112.273 | 11.9036 | 147.81 | 10.8791 | 219.847 | 6.283 | 239.351 | 11.5057 | 304.884 | 11.8561
33.0141 | 153.216 | 45.3284 | 40.9703 | 57.6814 | 23.3324 | 81.6085 | 12.1319 | 109.173 | 13.7336 | 143.873 | 12.4764 | 212.285 | 7.1552 | 233.675 | 12.9986 | 298.847 | 13.2083
33.0141 | 221.373 | 44.9223 | 48.6109 | 56.9364 | 27.7114 | 79.6732 | 14.0531 | 106.477 | 16.0682 | 140.602 | 14.2797 | 204.779 | 8.1404 | 229.736 | 14.5391 | 292.052 | 14.8328
33.0141 | 317.619 | 44.5643 | 58.724 | 56.3135 | 33.4431 | 77.9396 | 16.1004 | 104.578 | 18.3723 | 136.993 | 16.7742 | 198.528 | 9.2613 | 225.638 | 16.2622 | 285.411 | 16.909
32.9811 | 467.712 | 44.3864 | 72.519 | 55.7532 | 40.159 | 76.856 | 18.1713 | 102.507 | 21.474 | 134.012 | 19.4694 | 192.276 | 10.6636 | 221.834 | 18.2259 | 279.76 | 19.103
32.9481 | 545.582 | 44.1651 | 91.73 | 55.3642 | 49.4443 | 75.4095 | 21.3883 | 100.477 | 25.1748 | 130.312 | 23.5905 | 187.154 | 12.1562 | 216.574 | 21.3883 | 273.399 | 22.0617
32.9152 | 599.954 | 44.1651 | 121.613 | 55.1984 | 62.5426 | 74.1384 | 24.8745 | 98.5864 | 29.249 | 127.987 | 27.9061 | 182.168 | 14.3944 | 213.136 | 24.8497 | 266.648 | 26.1238
|  | 44.1651 | 157.252 | 55.1984 | 82.0107 | 73.1809 | 29.1322 | 97.4105 | 33.6781 | 125.578 | 33.0773 | 178.383 | 16.6572 | 209.334 | 29.543 | 262.154 | 29.7505
|  | 44.1651 | 198.314 | 55.1984 | 111.257 | 72.0913 | 34.4272 | 95.8643 | 39.9587 | 123.709 | 38.8166 | 174.501 | 19.3143 | 204.984 | 36.2285 | 257.735 | 34.7384
|  | 44.1651 | 274.198 | 55.1984 | 144.005 | 71.1602 | 41.4234 | 94.6261 | 46.8451 | 122.111 | 45.7342 | 170.193 | 23.3324 | 201.126 | 44.1171 | 253.644 | 39.3638
|  | 44.1651 | 357.399 | 55.1984 | 188.077 | 70.3817 | 50.3928 | 93.404 | 56.14 | 120.413 | 55.5814 | 167.491 | 27.7669 | 197.736 | 54.1007 | 249.868 | 45.4607
|  | 44.0768 | 437.402 | 55.1984 | 253.623 | 69.5422 | 61.3655 | 92.6597 | 66.0128 | 119.096 | 65.815 | 164.668 | 33.3096 | 195.182 | 63.4878 | 246.148 | 54.4808
|  | 44.0328 | 541.776 | 55.1984 | 345.451 | 68.9881 | 73.9101 | 91.8295 | 77.3893 | 117.558 | 81.9287 | 162.379 | 40.0387 | 192.853 | 74.2805 | 242.968 | 63.6149
|  | 43.9888 | 599.954 | 55.1984 | 466.777 | 68.3016 | 90.9081 | 91.0978 | 92.0056 | 116.155 | 103.218 | 160.442 | 47.1271 | 190.744 | 87.169 | 239.59 | 76.3898
|  |  |  | 55.1984 | 567.28 | 67.8252 | 113.732 | 90.5529 | 108.728 | 115.115 | 126.83 | 158.528 | 56.4214 | 188.28 | 102.601 | 236.26 | 91.6383
|  |  |  | 55.1432 | 599.954 | 67.4195 | 140.731 | 90.1012 | 131.611 | 113.514 | 168.149 | 156.48 | 67.8194 | 186.78 | 118.137 | 232.742 | 113.732
[6 empty] | 67.0162 | 180.161 | 89.7415 | 152.91 | 112.723 | 205.172 | 154.768 | 80.4672 | 185.106 | 137.119 | 229.736 | 135.89
[6 empty] | 66.7486 | 228.572 | 88.8486 | 188.265 | 112.16 | 254.895 | 152.312 | 103.012 | 183.631 | 161.394 | 227.223 | 161.879
[6 empty] | 66.4822 | 295.258 | 88.5824 | 239.332 | 111.601 | 314.458 | 150.345 | 130.692 | 181.804 | 191.876 | 224.512 | 196.733
[6 empty] | 66.283 | 365.714 | 88.1406 | 310.086 | 111.155 | 384.849 | 148.254 | 168.991 | 180.356 | 226.977 | 222.278 | 237.425
[6 empty] | 66.2168 | 452.077 | 88.0525 | 416.486 | 110.49 | 487.774 | 146.779 | 205.789 | 178.919 | 269.307 | 220.507 | 280.858
[6 empty] | 66.0845 | 540.153 | 88.0525 | 527.872 | 110.27 | 570.694 | 145.464 | 269.307 | 178.026 | 311.641 | 218.75 | 330.581
[6 empty] | 66.0845 | 599.954 | 88.0525 | 574.128 | 110.049 | 599.954 | 144.45 | 324.359 | 176.961 | 372.357 | 217.007 | 414.408
[8 empty] | 88.0525 | 599.954 |  |  | 143.585 | 405.797 | 175.903 | 451.625 | 215.925 | 497.131
[12 empty] | 143.012 | 502.127 | 175.2 | 532.111 | 215.709 | 566.713
[12 empty] | 142.584 | 572.981 | 174.501 | 574.128 | 215.278 | 599.954
[12 empty] | 142.584 | 599.954 | 173.978 | 599.954