## Sheet1
S&C Positrol Fuse Links: Universal and X-Performance "DR" Speed (TCC 175-6) | [9 empty] | S&C Positrol Fuse Links: Universal and X-Performance "DR" Speed (TCC 175-6)
Universal and Extra Performance Styles | [9 empty] | Universal and Extra Performance Styles
"DR" Speed (TCC 175-6) | [9 empty] | "DR" Speed (TCC 175-6)
Minimum Melting Time-Current Characteristic Curves Dated July 17, 2000 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated July 17, 2000
Tolerance in Terms of Current: Plus 10% within the coordinating range (melting times less than 10 seconds) | [9 empty] | Tolerance in Terms of Current: Plus 10% within the coordinating range (melting times less than 10 seconds)
3DR |  | 4DR |  | 5DR |  | 7DR |  | 10DR |  | 15DR |  | 20DR
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01 | 894.238 | 0.01
813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908 | 813.6833 | 0.011908
322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772 | 322.057 | 0.0772
215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405 | 215.776 | 0.17405
159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115 | 159.3359 | 0.32115
117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154 | 117.3226 | 0.61154
91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565 | 91.7359 | 1.0565
70.9132 | 1.8252 | 70.9132 | 1.8252 | 73.8109 | 1.7335 | 82.2867 | 1.4107 | 70.9132 | 1.8252 | 73.8109 | 1.7335 | 82.2867 | 1.4107
52.6651 | 3.5765 | 52.6651 | 3.5765 | 61.2868 | 2.7721 | 73.1801 | 1.955 | 52.6651 | 3.5765 | 61.2868 | 2.7721 | 73.1801 | 1.955
49.1707 | 4.2224 | 49.1707 | 4.2224 | 54.0386 | 3.8749 | 62.7056 | 3.3775 | 49.1707 | 4.2224 | 54.0386 | 3.8749 | 62.7056 | 3.3775
43.8543 | 4.9282 | 47.2403 | 4.654 | 47.3757 | 5.6865 | 59.5585 | 4.2588 | 47.2403 | 4.654 | 47.3757 | 5.6865 | 59.5585 | 4.2588
36.102 | 6.5054 | 38.7785 | 6.2678 | 42.7396 | 7.9944 | 57.5487 | 5.2336 | 40.9445 | 6.5804 | 42.7396 | 7.9944 | 57.5487 | 5.2336
26.7353 | 10.1674 | 31.4701 | 8.6615 | 35.6913 | 10.6439 | 50.7425 | 6.5054 | 32.8499 | 11.4008 | 39.3371 | 10.7665 | 52.5146 | 9.9088
22.4544 | 13.1175 | 23.1722 | 14.0906 | 28.8821 | 14.8357 | 42.0123 | 9.0415 | 31.2906 | 12.7839 | 36.102 | 15.8 | 47.2403 | 28.0888
18.8589 | 17.0208 | 18.913 | 19.5837 | 20.8449 | 25.1217 | 33.6103 | 13.3066 | 29.3821 | 15.3103 | 34.1922 | 22.8573 | 42.8621 | 102.7273
15.2174 | 24.1349 | 14.3302 | 31.5866 | 18.0152 | 32.3183 | 25.8331 | 21.2179 | 27.276 | 19.4719 | 32.3834 | 49.9354 | 40.5946 | 261.1901
12.0356 | 36.5514 | 11.4316 | 49.7927 | 15.5697 | 42.7837 | 20.6668 | 33.3521 | 25.2486 | 26.9854 | 31.2906 | 106.0133 | 40.2477 | 300.5188
9.6562 | 55.5144 | 10.7959 | 56.1537 | 13.5333 | 58.6173 | 18.0668 | 45.0459 | 23.9814 | 36.4469 | 30.2347 | 266.4765
7.7917 | 92.6684 | 9.8234 | 70.8067 | 11.8987 | 83.5946 | 16.2059 | 58.7853 | 22.7128 | 54.8824 | 30.0622 | 300.5188
7.0292 | 124.445 | 8.6368 | 101.8489 | 11.0774 | 105.4082 | 14.4537 | 84.3155 | 21.1452 | 125.1595
6.4143 | 176.9647 | 7.8364 | 144.8322 | 9.9649 | 168.5594 | 13.5721 | 110.3481 | 20.2571 | 261.1901
5.9206 | 265.7148 | 7.4858 | 182.6255 | 9.3304 | 271.0927 | 12.3142 | 202.4488 | 20.1415 | 300.5188
5.8365 | 300.5188 | 7.1919 | 243.1519 | 9.2242 | 300.5188 | 12.0356 | 264.1979
|  | 7.0898 | 300.5188 |  |  | 11.9669 | 300.5188