## 422_7MM
S&C Fault Fiter Electronic Power Fuses |  |  |  | S&C Fault Fiter Electronic Power Fuses
Underground-Subloop-Type Control Module (TCC 422-7) |  |  |  | Underground-Subloop-Type Control Module (TCC 422-7)
Minimum Tripping Time-Current Characteristic Curve Dated January 9, 1989 |  |  |  | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989
Tolerance in Terms of Current: Plus 10% |  |  |  | Tolerance: Curves are plotted to maximum test points. All variations are minus
Delay Band: 1 |  | Delay Band: 2 |  | Delay Band: 1 |  | Delay Band: 2
Min P/U = 500A |  | Min P/U = 400A |  | Min P/U = 500A |  | Min P/U = 400A
Current | Time | Current | Time | Current | Time | Current | Time
2979.44 | 0.01 | 2979.44 | 0.01 | 3967.95 | 0.01 | 3967.95 | 0.01
2979.44 | 0.012701 | 2979.44 | 0.01143 | 3967.95 | 0.013187 | 3967.95 | 0.012284
2979.44 | 0.018457 | 2979.44 | 0.016732 | 3967.95 | 0.018095 | 3967.95 | 0.016148
2979.44 | 0.028856 | 2979.44 | 0.028796 | 3967.95 | 0.023247 | 3967.95 | 0.021184
2979.44 | 0.050445 | 2979.44 | 0.049403 | 3967.95 | 0.025405 | 3967.95 | 0.025405
2979.44 | 0.06255 | 2979.44 | 0.062615 | 3777.65 | 0.027047 | 3777.65 | 0.027047
2812.92 | 0.067012 | 2979.44 | 0.083877 | 3722.75 | 0.030625 | 3722.75 | 0.030625
2641.86 | 0.071718 | 2979.44 | 0.11666 | 3676.33 | 0.034424 | 3676.33 | 0.034424
2499.43 | 0.076834 | 2812.92 | 0.12381 | 3427.58 | 0.036118 | 3427.58 | 0.036118
2359.74 | 0.082401 | 2658.49 | 0.13223 | 3427.58 | 0.042863 | 3427.58 | 0.042863
2213.92 | 0.08902 | 2507.29 | 0.14137 | 3427.58 | 0.058385 | 3427.58 | 0.058385
2092.38 | 0.095271 | 2359.74 | 0.15114 | 3427.58 | 0.075404 | 3427.58 | 0.078373
1946.73 | 0.10488 | 2193.19 | 0.16517 | 3172.36 | 0.081887 | 3427.58 | 0.1039
1811.22 | 0.11545 | 2040.52 | 0.18106 | 2957.71 | 0.087271 | 3427.58 | 0.12459
1692.2 | 0.12656 | 1890.56 | 0.19807 | 2777.85 | 0.09243 | 3246.19 | 0.13292
1589.29 | 0.13874 | 1764.48 | 0.21623 | 2617.12 | 0.0982 | 3061.56 | 0.14137
1491.09 | 0.1513 | 1622.88 | 0.24052 | 2468.27 | 0.10455 | 2893.47 | 0.15051
1409.22 | 0.16517 | 1503.61 | 0.26339 | 2313.32 | 0.11166 | 2703.34 | 0.16192
1344.45 | 0.17806 | 1404.81 | 0.28544 | 2143.31 | 0.12189 | 2491.61 | 0.17806
1294.78 | 0.1878 | 1340.24 | 0.30453 | 2000.38 | 0.13251 | 2248.92 | 0.20015
1294.78 | 0.23927 | 1294.78 | 0.31521 | 1884.63 | 0.14256 | 2066.29 | 0.22218
1294.78 | 0.3039 | 1294.78 | 0.38598 | 1715.36 | 0.15957 | 1888.58 | 0.24818
1294.78 | 0.42004 | 1294.78 | 0.5252 | 1621.19 | 0.17293 | 1729.77 | 0.27664
1294.78 | 0.57274 | 1294.78 | 0.65258 | 1525.79 | 0.18682 | 1558.03 | 0.31653
1294.78 | 0.78259 | 1246.94 | 0.68684 | 1470.95 | 0.19745 | 1434.5 | 0.34844
1294.78 | 1.1149 | 1180.95 | 0.74046 | 1434.5 | 0.20352 | 1434.5 | 0.44906
1294.78 | 1.4309 | 1094.16 | 0.83492 | 1434.5 | 0.24534 | 1434.5 | 0.57095
1227.54 | 1.5605 | 1020.13 | 0.93069 | 1434.5 | 0.29917 | 1434.5 | 0.67971
1179.72 | 1.6648 | 959.097 | 1.0288 | 1434.5 | 0.42711 | 1365.7 | 0.71688
1119.62 | 1.825 | 900.772 | 1.148 | 1434.5 | 0.60218 | 1286.68 | 0.77527
1061.48 | 2.0069 | 847.765 | 1.2824 | 1434.5 | 0.8669 | 1221.14 | 0.84722
1009.52 | 2.2 | 794.547 | 1.449 | 1434.5 | 1.1325 | 1156.51 | 0.92488
955.094 | 2.4678 | 749.357 | 1.627 | 1434.5 | 1.4429 | 1090.73 | 1.0096
911.193 | 2.7194 | 700.117 | 1.8949 | 1382.95 | 1.533 | 1034.09 | 1.1091
864.777 | 3.0568 | 656.167 | 2.1863 | 1327.68 | 1.6321 | 976.299 | 1.2299
825.027 | 3.4324 | 619.495 | 2.5516 | 1249.55 | 1.8231 | 919.809 | 1.3767
791.231 | 3.826 | 584.872 | 3.0061 | 1176.02 | 2.0111 | 839.824 | 1.6389
744.67 | 4.5454 | 559.156 | 3.4288 | 1117.28 | 2.2162 | 788.753 | 1.8929
702.317 | 5.4908 | 540.191 | 3.9109 | 1044.96 | 2.5437 | 733.081 | 2.2371
669.334 | 6.5573 | 516.98 | 4.6607 | 989.661 | 2.8562 | 684.911 | 2.6772
641.245 | 7.7576 | 498.401 | 5.5138 | 939.248 | 3.2273 | 652.746 | 3.1278
618.847 | 9.2256 | 479.487 | 6.7377 | 897.951 | 3.5975 | 619.495 | 3.7197
596.608 | 11.4155 | 463.223 | 8.1989 | 862.068 | 3.9976 | 593.497 | 4.3822
574.567 | 14.7276 | 447.512 | 10.6442 | 825.027 | 4.517 | 570.973 | 5.1467
559.156 | 18.5692 | 436.877 | 12.7914 | 798.712 | 5.0141 | 544.728 | 6.3154
548.157 | 22.8336 | 426.942 | 15.7618 | 765.193 | 5.8093 | 525.153 | 7.4714
536.251 | 29.3971 | 418.106 | 20.1027 | 735.384 | 6.7166 | 504.695 | 9.168
528.458 | 37.3371 | 410.31 | 25.7465 | 711.929 | 7.653 | 489.108 | 11.1562
524.604 | 45.5295 | 406.892 | 32.1924 | 692.834 | 8.7563 | 473.013 | 14.3781
519.69 | 58.8623 | 406.466 | 40.5473 | 673.547 | 10.1769 | 464.679 | 17.1527
513.747 | 83.4226 | 406.466 | 54.2587 | 656.854 | 11.828 | 457.447 | 20.3774
508.934 | 113.988 | 406.466 | 71.1807 | 642.587 | 13.6326 | 451.743 | 25.3729
507.871 | 157.881 | 406.466 | 96.1503 | 627.317 | 16.1617 | 443.784 | 31.4614
506.81 | 198.649 | 406.466 | 138.854 | 615.62 | 19.3409 | 441.931 | 38.1648
506.81 | 250.204 | 406.466 | 159.205 | 607.944 | 22.2918 | 439.627 | 48.9816
506.81 | 373.215 | 406.466 | 209.951 | 598.483 | 26.985 | 439.627 | 69.0578
506.81 | 528.387 | 406.466 | 284.193 | 590.402 | 33.2167 | 439.627 | 94.4588
506.81 | 676.025 | 406.466 | 370.111 | 583.65 | 40.21 | 439.627 | 109.211
506.81 | 885.01 | 406.466 | 504.663 | 579.393 | 49.238 | 439.627 | 157.716
506.81 | 1000 | 406.466 | 631.669 | 574.567 | 60.7352 | 439.627 | 237.23
|  | 406.466 | 805.637 | 569.78 | 76.3382 | 439.627 | 318.115
|  | 406.466 | 1001.04 | 567.996 | 95.1517 | 439.627 | 431.956
|  |  |  | 564.443 | 129.472 | 439.627 | 584.703
|  |  |  | 564.443 | 180.455 | 439.627 | 759.09
|  |  |  | 564.443 | 250.727 | 439.627 | 935.363
|  |  |  | 564.443 | 362.084 | 439.627 | 1000
|  |  |  | 564.443 | 533.376
|  |  |  | 564.443 | 734.915
|  |  |  | 564.443 | 1000