## 60 Hz, 660-1 CT Ratio
S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0
S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018
60 Hz, 660:1 CT Ratio | [11 empty] | 60 Hz, 660:1 CT Ratio | [11 empty] | 60 Hz, 660:1 CT Ratio | [11 empty] | 60 Hz, 660:1 CT Ratio | [11 empty] | 60 Hz, 660:1 CT Ratio | [11 empty] | 60 Hz, 660:1 CT Ratio
Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information.
8K |  |  |  | 10K |  |  |  | 12K |  |  |  | 15K |  |  |  | 20K |  |  |  | 25K |  |  |  | 30K |  |  |  | 40K |  |  |  | 50K |  |  |  | 65K |  |  |  | 80K |  |  |  | 100K |  |  |  | 125K |  |  |  | 150K |  |  |  | 175K |  |  |  | 200K
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
15.601 | 1000 | 18.904 | 1000 | 20.396 | 1000 | 23.721 | 1000 | 27.313 | 1000 | 30.488 | 1000 | 32.896 | 1000 | 36.942 | 1000 | 42.451 | 1000 | 47.911 | 1000 | 49.597 | 1000 | 55.42 | 1000 | 59.915 | 1000 | 67.893 | 1000 | 79.594 | 1000 | 89.205 | 1000 | 97.997 | 1000 | 109.06 | 1000 | 128.37 | 1000 | 143.3 | 1000 | 159.32 | 1000 | 178.03 | 1000 | 195.18 | 1000 | 217.44 | 1000 | 274.55 | 1000 | 312.55 | 1000 | 329.65 | 1000 | 378.1 | 1000 | 401.85 | 1000 | 448.4 | 1000 | 479.75 | 1000 | 570 | 1000
15.601 | 302.73 | 18.904 | 41.674 | 20.396 | 302.43 | 23.721 | 31.681 | 27.313 | 303.64 | 30.488 | 242.979 | 32.896 | 300.92 | 36.942 | 147.519 | 42.451 | 303.64 | 47.911 | 161.599 | 49.597 | 602.96 | 55.42 | 490.149 | 59.915 | 608.41 | 67.893 | 81.774 | 79.594 | 609.02 | 89.205 | 452.689 | 97.997 | 602.36 | 109.06 | 557.549 | 128.37 | 601.76 | 143.3 | 274.409 | 159.32 | 605.98 | 178.03 | 538.399 | 195.18 | 601.15 | 217.44 | 569.259 | 274.55 | 600 | 312.55 | 170.109 | 329.65 | 600 | 378.1 | 164.259 | 401.85 | 600 | 448.4 | 559.789 | 479.75 | 600 | 570 | 162.329
15.742 | 49.891 | 19.285 | 28.471 | 20.437 | 116.85 | 24.127 | 20.643 | 27.34 | 270.66 | 31.104 | 96.608 | 32.962 | 270.93 | 37.5 | 75.519 | 42.621 | 261.09 | 48.684 | 94.887 | 49.996 | 26.492 | 57.165 | 18.014 | 60.156 | 161.23 | 69.612 | 40.642 | 79.753 | 578.16 | 90.462 | 246.119 | 98.095 | 568.98 | 110.38 | 322.719 | 128.5 | 569.55 | 145.03 | 129.799 | 159.96 | 559.39 | 181.08 | 308.659 | 195.96 | 553.83 | 220.29 | 351.899 | 275.5 | 300 | 340.1 | 64.209 | 332.5 | 300 | 408.5 | 66.843 | 413.25 | 300 | 482.6 | 150.709 | 494 | 300 | 625.1 | 64.79
15.869 | 42.515 | 19.833 | 20.078 | 20.457 | 94.618 | 24.738 | 14.595 | 27.449 | 226.98 | 31.574 | 42.195 | 33.061 | 223.15 | 38.029 | 44.968 | 42.835 | 212.91 | 49.519 | 45.224 | 50.599 | 22.04 | 58.67 | 14.518 | 60.336 | 117.2 | 71.517 | 25.39 | 79.913 | 513.81 | 92.752 | 96.975 | 98.389 | 488.26 | 112.05 | 102.719 | 128.5 | 461.21 | 146.78 | 94.061 | 160.44 | 498.62 | 184.37 | 184.099 | 196.75 | 446.68 | 222.95 | 241.709 | 277.4 | 200 | 365.75 | 36.992 | 334.4 | 200 | 446.5 | 35.771 | 422.75 | 200 | 517.75 | 72.508 | 503.5 | 200 | 682.1 | 34.271
15.996 | 35.796 | 20.437 | 14.753 | 20.478 | 78.48 | 25.491 | 10.222 | 27.559 | 188.83 | 32.438 | 17.121 | 33.16 | 181.43 | 38.565 | 34.532 | 43.049 | 167.81 | 50.62 | 28.278 | 51.415 | 18.063 | 60.336 | 11.532 | 60.821 | 88.31 | 73.474 | 18.522 | 80.313 | 422.36 | 94.532 | 61.887 | 98.685 | 424.48 | 113.63 | 66.198 | 128.5 | 359.55 | 148.7 | 69.508 | 161.41 | 415.24 | 187.72 | 113.959 | 197.93 | 362.07 | 225.64 | 185.449 | 287.85 | 100 | 427.5 | 15.999 | 348.65 | 100 | 515.85 | 16.613 | 448.4 | 100 | 555.75 | 39.667 | 530.1 | 100 | 798 | 15.955
16.189 | 29.84 | 21.144 | 10.949 | 20.519 | 63.998 | 26.373 | 7.8567 | 27.67 | 150.78 | 33.36 | 12.074 | 33.226 | 149.58 | 39.109 | 26.976 | 43.222 | 135.08 | 51.643 | 20.017 | 52.349 | 15.224 | 62.298 | 9.75 | 61.248 | 67.684 | 75.787 | 13.748 | 80.716 | 336.25 | 96.249 | 41.64 | 99.081 | 347.88 | 115.11 | 46.687 | 128.89 | 278.62 | 150.8 | 50.542 | 162.54 | 325.99 | 191.7 | 79.514 | 198.93 | 299.12 | 228.82 | 141.939 | 312.55 | 50 | 513 | 7.4923 | 378.1 | 50 | 617.5 | 7.5333 | 482.6 | 50 | 647.9 | 16.126 | 570 | 50 | 950 | 7.6302
16.401 | 25.735 | 21.919 | 8.1881 | 20.498 | 52.24 | 27.231 | 6.2353 | 27.836 | 119.56 | 34.273 | 9.9614 | 33.36 | 119.68 | 39.899 | 19.988 | 43.526 | 107.97 | 52.844 | 15.62 | 53.353 | 13.129 | 64.582 | 8.3557 | 61.74 | 54.209 | 77.706 | 11.372 | 81.283 | 255.66 | 98.193 | 29.509 | 99.478 | 282.55 | 116.86 | 33.143 | 129.01 | 216.34 | 152.77 | 38.814 | 163.68 | 258.75 | 195.96 | 54.625 | 200.12 | 251.6 | 232.04 | 112.819 | 340.1 | 30 | 595.65 | 4.3303 | 408.5 | 30 | 717.25 | 4.3265 | 517.75 | 30 | 779 | 7.4607 | 625.1 | 30 | 1102 | 4.3403
16.632 | 21.799 | 22.836 | 6.4091 | 20.519 | 45.461 | 27.948 | 5.4731 | 27.948 | 100.17 | 35.281 | 8.1124 | 33.493 | 99.768 | 40.705 | 16.098 | 43.831 | 85.528 | 54.182 | 12.052 | 54.16 | 11.645 | 66.949 | 7.2326 | 62.298 | 43.417 | 80.153 | 9.2222 | 81.69 | 201.51 | 100.08 | 23.27 | 99.677 | 223.6 | 118.74 | 24.695 | 129.4 | 170.69 | 155.23 | 31.524 | 164.83 | 207.03 | 199.92 | 40.811 | 201.33 | 209.11 | 235.32 | 92.087 | 365.75 | 20 | 674.5 | 2.8491 | 446.5 | 20 | 807.5 | 2.8969 | 555.75 | 20 | 902.5 | 4.3537 | 682.1 | 20 | 1244.5 | 2.8708
16.917 | 18.557 | 23.626 | 5.3937 | 20.56 | 38.086 | 28.944 | 4.6726 | 28.088 | 79.986 | 36.319 | 6.7955 | 33.594 | 81.683 | 41.652 | 13.148 | 43.963 | 69.467 | 55.498 | 10.0012 | 55.42 | 10.205 | 69.403 | 6.2399 | 62.924 | 35.299 | 82.346 | 7.8024 | 82.182 | 155.07 | 102.4 | 18.068 | 99.976 | 173.79 | 120.53 | 20.444 | 129.92 | 141.01 | 158.21 | 24.942 | 166.16 | 159.31 | 203.76 | 30.821 | 203.35 | 178.19 | 238.63 | 76.116 | 427.5 | 10 | 855 | 1.3897 | 515.85 | 10 | 1026 | 1.3856 | 647.9 | 10 | 1035.5 | 2.7579 | 798 | 10 | 1577 | 1.3903
17.19 | 16.068 | 24.788 | 4.323 | 20.684 | 32.293 | 30.095 | 3.9818 | 28.201 | 64.062 | 37.313 | 5.8851 | 33.762 | 67.549 | 42.664 | 10.653 | 44.272 | 55.249 | 56.903 | 8.3825 | 57.165 | 8.8804 | 73.401 | 5.2035 | 63.493 | 30.412 | 84.769 | 6.6148 | 82.594 | 126.58 | 103.95 | 15.174 | 100.28 | 127.47 | 122.85 | 15.797 | 130.97 | 115.45 | 160.44 | 21.016 | 167.99 | 124.19 | 207.67 | 25.129 | 205.39 | 146.77 | 243.7 | 59.009 | 513 | 5 | 1092.5 | 0.70254 | 617.5 | 5 | 1320.5 | 0.69682 | 779 | 5 | 1301.5 | 1.4053 | 950 | 5 | 2042.5 | 0.69212
17.468 | 14.011 | 25.851 | 3.5958 | 20.746 | 28.271 | 31.26 | 3.4389 | 28.285 | 52.66 | 38.488 | 5.0577 | 33.932 | 55.693 | 43.875 | 8.6918 | 44.538 | 45.597 | 58.46 | 7.1152 | 58.67 | 7.9236 | 77.396 | 4.4028 | 64.067 | 26.466 | 87.438 | 5.7058 | 83.091 | 104.88 | 106.58 | 12.08 | 100.68 | 105.94 | 125.08 | 13.473 | 131.75 | 98.087 | 163.68 | 17.003 | 170.36 | 94.903 | 211.65 | 20.167 | 207.46 | 122.1 | 247.63 | 50.071 | 595.65 | 3 | 1349 | 0.41622 | 717.25 | 3 | 1615 | 0.42094 | 902.5 | 3 | 1681.5 | 0.69394 | 1102 | 3 | 2508 | 0.41891
17.803 | 12.096 | 27.014 | 3.0234 | 20.85 | 24.553 | 32.601 | 3.0184 | 28.37 | 43.243 | 39.344 | 4.5715 | 34.17 | 45.917 | 45.076 | 7.4262 | 44.941 | 37.146 | 60.18 | 6.0812 | 60.336 | 7.0628 | 81.69 | 3.7816 | 64.906 | 22.507 | 90.734 | 4.9085 | 83.675 | 85.871 | 108.85 | 10.167 | 101.18 | 86.995 | 127.22 | 11.449 | 132.94 | 76.39 | 166.82 | 14.504 | 172.59 | 75.554 | 215.71 | 16.501 | 209.96 | 101.58 | 251.62 | 41.395 | 674.5 | 2 | 1615 | 0.28258 | 807.5 | 2 | 1947.5 | 0.28027 | 1035.5 | 2 | 2061.5 | 0.4197 | 1244.5 | 2 | 2973.5 | 0.28604
18.162 | 10.473 | 28.314 | 2.5415 | 21.102 | 20.839 | 33.796 | 2.7108 | 28.484 | 35.868 | 40.786 | 3.8823 | 34.376 | 38.584 | 46.263 | 6.4524 | 45.347 | 29.721 | 62.075 | 5.1133 | 62.298 | 6.2641 | 84.854 | 3.4244 | 65.492 | 19.942 | 94.248 | 4.1819 | 84.6 | 67.145 | 111.27 | 8.5035 | 101.49 | 74.877 | 129.4 | 10.077 | 134.01 | 64.062 | 170.36 | 12.279 | 175.2 | 59.196 | 221.17 | 13.576 | 212.29 | 88.752 | 255.94 | 34.89 | 855 | 1 | 2194.5 | 0.15589 | 1026 | 1 | 2669.5 | 0.15506 | 1301.5 | 1 | 2479.5 | 0.28107 | 1577 | 1 | 4085 | 0.15485
18.529 | 9.1967 | 29.676 | 2.1685 | 21.292 | 18.026 | 35.564 | 2.3516 | 28.627 | 29.9 | 42.028 | 3.4193 | 34.756 | 32.683 | 47.959 | 5.3534 | 45.849 | 23.923 | 64.351 | 4.3759 | 64.582 | 5.5392 | 90.011 | 2.9333 | 66.349 | 17.705 | 98.291 | 3.6304 | 85.365 | 52.712 | 113.86 | 7.2896 | 102.3 | 61.121 | 131.62 | 8.9125 | 135.09 | 53.455 | 173.8 | 10.715 | 178.03 | 45.872 | 225.86 | 11.434 | 214.63 | 76.619 | 260.85 | 29 | 1092.5 | 0.5 | 3040 | 0.091559 | 1320.5 | 0.5 | 3676.5 | 0.091815 | 1681.5 | 0.5 | 3391.5 | 0.15526 | 2042.5 | 0.5 | 5633.5 | 0.091755
18.904 | 8.1894 | 31.323 | 1.8432 | 21.549 | 15.531 | 37.053 | 2.1004 | 28.742 | 25.709 | 43.308 | 3.0627 | 35 | 28.555 | 49.767 | 4.5674 | 46.449 | 20.102 | 66.709 | 3.8261 | 66.949 | 4.9424 | 95.196 | 2.5428 | 67.893 | 14.152 | 102.82 | 3.1778 | 86.395 | 42.985 | 117.09 | 6.1416 | 102.81 | 51.876 | 134.15 | 7.6762 | 136.86 | 40.766 | 177.85 | 9.3575 | 181.08 | 34.843 | 229.97 | 9.9804 | 217.44 | 64.447 | 265.85 | 23.686 | 1349 | 0.3 | 3895 | 0.069 | 1615 | 0.3 | 4655 | 0.069 | 2061.5 | 0.3 | 4702.5 | 0.09152 | 2508 | 0.3 | 7172.5 | 0.069
19.285 | 7.2199 | 32.962 | 1.5898 | 21.788 | 13.611 | 38.642 | 1.8761 | 28.857 | 21.93 | 45.211 | 2.6468 | 35.387 | 23.923 | 51.901 | 3.7955 | 47.151 | 16.691 | 69.71 | 3.2546 | 69.403 | 4.4187 | 99.976 | 2.2706 | 69.612 | 11.668 | 107.98 | 2.7653 | 87.089 | 36.739 | 122.11 | 4.9277 | 103.64 | 42.728 | 136.86 | 6.8372 | 138.51 | 34.29 | 181.8 | 8.1299 | 184.37 | 28.47 | 234.38 | 8.6768 | 220.29 | 56.252 | 270.95 | 19.936 | 1615 | 0.2 | 4655 | 0.059 | 1947.5 | 0.2 | 5605 | 0.059 | 2479.5 | 0.2 | 5937.5 | 0.069 | 2973.5 | 0.2 | 8645 | 0.059
19.833 | 6.3843 | 34.652 | 1.3831 | 22.117 | 11.797 | 40.219 | 1.698 | 28.973 | 19.295 | 47.198 | 2.281 | 35.85 | 20.244 | 54.02 | 3.3179 | 47.911 | 14.095 | 72.919 | 2.8399 | 73.401 | 3.7691 | 106.26 | 1.9623 | 71.517 | 9.6296 | 113.17 | 2.4305 | 88.229 | 29.99 | 126.97 | 4.1405 | 104.47 | 35.796 | 140.74 | 5.8794 | 140.18 | 29.161 | 186.41 | 7.0139 | 187.72 | 22.756 | 240.07 | 7.3528 | 222.95 | 48.417 | 277.25 | 16.479 | 2194.5 | 0.1 | 6460 | 0.049 | 2669.5 | 0.1 | 7695 | 0.049 | 3391.5 | 0.1 | 7125 | 0.059 | 4085 | 0.1 | 11970 | 0.049
20.437 | 5.5614 | 36.611 | 1.1956 | 22.429 | 10.359 | 41.903 | 1.5319 | 29.118 | 17.476 | 49.419 | 1.993 | 36.392 | 16.909 | 56.903 | 2.8002 | 48.684 | 12.156 | 76.428 | 2.4776 | 77.396 | 3.2539 | 111.94 | 1.7494 | 73.474 | 8.1079 | 118.86 | 2.1502 | 89.205 | 25.479 | 131.62 | 3.6373 | 105.63 | 29.573 | 145.61 | 4.9607 | 141.73 | 25.942 | 190.55 | 6.2698 | 191.7 | 18.135 | 244.19 | 6.7221 | 225.64 | 42.813 | 282.85 | 14.192 | 3040 | 0.05 | 6461 | 0.045 | 3676.5 | 0.05 | 7696 | 0.045 | 4702.5 | 0.05 | 9880 | 0.049 | 5633.5 | 0.05 | 11971 | 0.045
21.144 | 4.7915 | 38.797 | 1.021 | 22.768 | 9.2243 | 43.352 | 1.4117 | 29.41 | 15.269 | 51.953 | 1.7363 | 36.942 | 14.51 | 59.582 | 2.4548 | 49.519 | 10.515 | 80.668 | 2.1306 | 81.69 | 2.8316 | 119.45 | 1.5102 | 75.787 | 6.7791 | 124.58 | 1.9103 | 90.462 | 21.176 | 136.72 | 3.2281 | 106.58 | 25.326 | 151.1 | 4.2563 | 143.3 | 22.328 | 196.75 | 5.4576 | 195.96 | 15.133 | 252.38 | 5.5737 | 228.82 | 37.034 | 287.99 | 12.381 | 3895 | 0.03 | 9000 | 0.045 | 4655 | 0.03 | 12000 | 0.045 | 5937.5 | 0.03 | 9881 | 0.045 | 7172.5 | 0.03 | 17500 | 0.045
21.919 | 4.1572 | 41.527 | 0.86807 | 23.112 | 8.2717 | 45.438 | 1.2579 | 29.647 | 13.761 | 54.399 | 1.531 | 37.5 | 12.589 | 62.636 | 2.1327 | 50.62 | 8.916 | 84.974 | 1.8333 | 84.854 | 2.5724 | 128.12 | 1.3035 | 77.706 | 5.9706 | 132.15 | 1.6489 | 92.752 | 16.23 | 141.16 | 2.924 | 107.66 | 21.908 | 157.74 | 3.6806 | 145.03 | 19.665 | 204.16 | 4.6521 | 199.92 | 12.729 | 258.51 | 4.8869 | 232.04 | 32.068 | 292.93 | 10.889 | 4655 | 0.02 | 12920 | 0.045 | 5605 | 0.02 | 15390 | 0.045 | 7125 | 0.02 | 15000 | 0.045 | 8645 | 0.02 | 23940 | 0.045
22.836 | 3.5746 | 44.095 | 0.75439 | 23.391 | 7.6205 | 47.815 | 1.1182 | 30.005 | 12.096 | 56.96 | 1.353 | 38.029 | 11.267 | 65.258 | 1.8977 | 51.643 | 7.79 | 88.885 | 1.6339 | 90.011 | 2.2341 | 137.13 | 1.1333 | 80.153 | 5.2218 | 139.9 | 1.449 | 94.532 | 13.368 | 145.9 | 2.6611 | 109.06 | 18.706 | 165.16 | 3.1874 | 146.78 | 17.424 | 210.59 | 4.1701 | 203.76 | 10.988 | 269.06 | 4.0808 | 235.32 | 27.711 | 299.44 | 9.4549 | 6460 | 0.01 | 12921 | 0.043 | 7695 | 0.01 | 15391 | 0.043 | 9880 | 0.01 | 19760 | 0.045 | 11970 | 0.01 | 23941 | 0.043
23.626 | 3.1545 | 47.529 | 0.63897 | 23.721 | 6.916 | 50.671 | 0.97706 | 30.488 | 10.653 | 59.88 | 1.1914 | 38.565 | 10.164 | 68.879 | 1.6454 | 52.844 | 6.7927 | 94.57 | 1.3935 | 95.196 | 1.9539 | 146.93 | 0.98973 | 82.346 | 4.6499 | 149 | 1.2571 | 96.249 | 11.38 | 150.19 | 2.4379 | 110.38 | 15.972 | 172.59 | 2.7859 | 148.7 | 15.438 | 218.1 | 3.6997 | 207.67 | 9.4863 | 277.25 | 3.5902 | 238.63 | 24.163 | 305.8 | 8.3741 |  |  | 20000 | 0.043 |  |  | 20000 | 0.043 |  |  | 19761 | 0.043 |  |  | 25000 | 0.043
24.788 | 2.6801 | 50.823 | 0.55213 | 24.127 | 6.3145 | 53.75 | 0.85875 | 31.104 | 9.2613 | 63.329 | 1.0374 | 39.109 | 9.1234 | 71.833 | 1.4726 | 54.182 | 5.9289 | 100.72 | 1.1932 | 99.976 | 1.7504 | 159.64 | 0.8391 | 84.769 | 4.1614 | 157.74 | 1.1116 | 98.193 | 9.8143 | 155.39 | 2.2225 | 112.05 | 13.913 | 178.92 | 2.5199 | 150.8 | 13.969 | 224.51 | 3.3655 | 211.65 | 8.3549 | 289.44 | 3.069 | 243.7 | 20.002 | 312.29 | 7.3855 |  |  | 25000 | 0.043 |  |  | 25000 | 0.043 |  |  | 22500 | 0.043
25.851 | 2.351 | 55.332 | 0.46299 | 24.738 | 5.6285 | 57.705 | 0.73807 | 31.574 | 8.3298 | 67.38 | 0.89984 | 39.899 | 8.0433 | 74.84 | 1.3261 | 55.498 | 5.2218 | 107.06 | 1.0357 | 106.26 | 1.5187 | 174.85 | 0.7064 | 87.438 | 3.7279 | 171.56 | 0.93136 | 100.08 | 8.5066 | 160.28 | 2.0443 | 113.63 | 12.023 | 186.03 | 2.2621 | 152.77 | 12.526 | 231.58 | 3.0773 | 215.71 | 7.3879 | 300.64 | 2.7375 | 247.63 | 17.354 | 318.28 | 6.7235 | [10 empty] | 25000 | 0.043
27.014 | 2.0541 | 59.761 | 0.39646 | 25.491 | 4.9523 | 63.076 | 0.61488 | 32.438 | 7.0276 | 71.332 | 0.79409 | 40.705 | 7.1552 | 79.547 | 1.1487 | 56.903 | 4.6313 | 113.11 | 0.91302 | 111.94 | 1.3551 | 193.24 | 0.58568 | 90.734 | 3.3262 | 192.28 | 0.73827 | 102.4 | 7.2852 | 166.49 | 1.8454 | 115.11 | 10.814 | 193.43 | 2.034 | 155.23 | 11.166 | 239.35 | 2.7848 | 221.17 | 6.4292 | 311.04 | 2.4623 | 251.62 | 15.285 | 326.99 | 5.8072
28.314 | 1.7804 | 64.932 | 0.33662 | 26.373 | 4.3269 | 69.501 | 0.50443 | 33.36 | 6.0427 | 74.989 | 0.70961 | 41.652 | 6.3525 | 84.044 | 1.0097 | 58.46 | 4.1489 | 121.55 | 0.78086 | 119.45 | 1.1816 | 219.63 | 0.462 | 94.248 | 2.9708 | 210.17 | 0.62381 | 103.95 | 6.5133 | 173.11 | 1.6747 | 116.86 | 9.6296 | 203.35 | 1.7887 | 158.21 | 9.9428 | 246.15 | 2.5726 | 225.86 | 5.6908 | 322.44 | 2.2275 | 255.94 | 13.354 | 335.27 | 5.175
29.676 | 1.554 | 71.261 | 0.28182 | 27.231 | 3.8723 | 74.392 | 0.44106 | 34.273 | 5.269 | 79.946 | 0.62177 | 42.664 | 5.5892 | 90.138 | 0.86265 | 60.18 | 3.6945 | 129.59 | 0.68114 | 128.12 | 1.0252 | 238.16 | 0.39836 | 98.291 | 2.6349 | 230.66 | 0.52287 | 106.58 | 5.7136 | 180.54 | 1.5062 | 118.74 | 8.5749 | 211.65 | 1.6193 | 160.44 | 8.9338 | 256.71 | 2.2859 | 229.97 | 5.1031 | 333.93 | 2.0323 | 260.85 | 11.552 | 345.48 | 4.5683
31.323 | 1.3349 | 78.598 | 0.23582 | 27.948 | 3.4793 | 79.15 | 0.39035 | 35.281 | 4.6128 | 87.212 | 0.51982 | 43.875 | 4.9177 | 98.627 | 0.71098 | 62.075 | 3.3296 | 137.6 | 0.60104 | 137.13 | 0.88767 | 260.32 | 0.33947 | 102.82 | 2.3463 | 249.37 | 0.4524 | 108.85 | 5.0827 | 189.41 | 1.3473 | 120.53 | 7.7125 | 222.5 | 1.4377 | 163.68 | 7.9633 | 269.6 | 1.9838 | 234.38 | 4.636 | 347.56 | 1.8228 | 265.85 | 10.154 | 358.14 | 3.9367
32.962 | 1.1593 | 87.825 | 0.19372 | 28.944 | 3.1107 | 84.213 | 0.3467 | 36.319 | 4.0142 | 94.855 | 0.44078 | 45.076 | 4.3529 | 107.27 | 0.59403 | 64.351 | 2.9768 | 145.96 | 0.53504 | 146.93 | 0.77402 | 282.57 | 0.29318 | 107.98 | 2.0623 | 275.6 | 0.37606 | 111.27 | 4.5533 | 201.33 | 1.1674 | 122.85 | 6.8953 | 233.44 | 1.2887 | 166.82 | 7.1624 | 282.01 | 1.7669 | 240.07 | 4.1822 | 359.22 | 1.6781 | 270.95 | 9.0507 | 370.16 | 3.5091
34.652 | 1.0109 | 96.965 | 0.16394 | 30.095 | 2.7645 | 89.958 | 0.30551 | 37.313 | 3.5603 | 101.83 | 0.38481 | 46.263 | 3.8878 | 120.34 | 0.46957 | 66.709 | 2.6747 | 157.01 | 0.46198 | 159.64 | 0.65892 | 303.36 | 0.25848 | 113.17 | 1.8255 | 294.4 | 0.33256 | 113.86 | 4.1614 | 213.35 | 1.0272 | 125.08 | 6.1709 | 244.43 | 1.1577 | 170.36 | 6.4163 | 297.65 | 1.5511 | 244.19 | 3.8299 | 370.9 | 1.5543 | 277.25 | 7.8605 | 382.96 | 3.1337
36.611 | 0.88147 | 107.38 | 0.13909 | 31.26 | 2.4765 | 96.771 | 0.26762 | 38.488 | 3.1672 | 110.21 | 0.33173 | 47.959 | 3.431 | 132.2 | 0.39091 | 69.71 | 2.3557 | 166.39 | 0.41258 | 174.85 | 0.55202 | 322.44 | 0.23267 | 118.86 | 1.6223 | 319.24 | 0.28735 | 117.09 | 3.7428 | 224.51 | 0.91935 | 127.22 | 5.6173 | 258.25 | 1.0278 | 173.8 | 5.8348 | 316.06 | 1.3403 | 252.38 | 3.4104 | 385.65 | 1.4089 | 282.85 | 7.1053 | 399.79 | 2.7486
38.797 | 0.76479 | 119.03 | 0.11837 | 32.601 | 2.1986 | 104.73 | 0.23221 | 39.344 | 2.912 | 119.14 | 0.2877 | 49.767 | 3.0127 | 143.07 | 0.33549 | 72.919 | 2.0665 | 178.1 | 0.36173 | 193.24 | 0.45241 | 355.29 | 0.19734 | 124.58 | 1.4548 | 340.68 | 0.2554 | 122.11 | 3.2734 | 234.38 | 0.84006 | 129.4 | 5.1647 | 270.95 | 0.92996 | 177.85 | 5.2375 | 334.26 | 1.1794 | 258.51 | 3.1107 | 399.39 | 1.2931 | 287.99 | 6.4485 | 414.86 | 2.4659
41.527 | 0.65236 | 132.73 | 0.10084 | 33.796 | 1.9854 | 116.2 | 0.19338 | 40.786 | 2.5698 | 130.24 | 0.24501 | 51.901 | 2.664 | 155.76 | 0.28691 | 76.428 | 1.8073 | 191.97 | 0.31456 | 219.63 | 0.35304 | 382.96 | 0.17379 | 132.15 | 1.2685 | 367.94 | 0.22338 | 126.97 | 2.9004 | 242.97 | 0.77677 | 131.62 | 4.7628 | 285.7 | 0.83422 | 181.8 | 4.7915 | 354.23 | 1.0387 | 269.06 | 2.7534 | 419.44 | 1.1607 | 292.93 | 5.8935 | 429.63 | 2.2328
44.095 | 0.56713 | 146.55 | 0.087957 | 35.564 | 1.7452 | 128.3 | 0.16442 | 42.028 | 2.323 | 141.65 | 0.2115 | 54.02 | 2.3723 | 171.46 | 0.24154 | 80.668 | 1.5634 | 210.68 | 0.26567 | 238.16 | 0.30054 | 412.79 | 0.15387 | 139.9 | 1.1172 | 397.39 | 0.19549 | 131.62 | 2.5905 | 252.88 | 0.71549 | 134.15 | 4.4231 | 300.35 | 0.75271 | 186.41 | 4.3704 | 379.91 | 0.89384 | 277.25 | 2.4989 | 445.83 | 1.005 | 299.44 | 5.306 | 441.83 | 2.0699
47.529 | 0.48039 | 162.44 | 0.077962 | 37.053 | 1.5696 | 140.8 | 0.14085 | 43.308 | 2.1188 | 156.23 | 0.17923 | 56.903 | 2.0377 | 190.44 | 0.20123 | 84.974 | 1.37 | 235.65 | 0.21827 | 260.32 | 0.25179 | 449.41 | 0.13464 | 149 | 0.9732 | 430.49 | 0.17083 | 136.72 | 2.3299 | 267.45 | 0.63939 | 136.86 | 4.0953 | 312.6 | 0.69407 | 190.55 | 4.0182 | 400.59 | 0.79772 | 289.44 | 2.2141 | 473.87 | 0.88259 | 305.8 | 4.83 | 458.49 | 1.8745
50.823 | 0.41472 | 177.39 | 0.071772 | 38.642 | 1.416 | 156.86 | 0.1193 | 45.211 | 1.8754 | 171.29 | 0.15389 | 59.582 | 1.7929 | 207.13 | 0.17475 | 88.885 | 1.22 | 266.23 | 0.17706 | 282.57 | 0.21477 | 491.73 | 0.1171 | 157.74 | 0.86316 | 466.35 | 0.14998 | 141.16 | 2.1337 | 277.81 | 0.59182 | 140.74 | 3.7503 | 328.63 | 0.62955 | 196.75 | 3.6105 | 427.92 | 0.69439 | 300.64 | 1.9914 | 501.66 | 0.78308 | 312.29 | 4.4099 | 482.48 | 1.6323
55.332 | 0.34502 | 201.01 | 0.064472 | 40.219 | 1.2787 | 173.53 | 0.10287 | 47.198 | 1.6567 | 191.01 | 0.12981 | 62.636 | 1.5634 | 225.96 | 0.15128 | 94.57 | 1.0511 | 300.77 | 0.14514 | 303.36 | 0.1869 | 551.11 | 0.099273 | 171.56 | 0.72169 | 498.17 | 0.13502 | 145.9 | 1.9422 | 291.47 | 0.53803 | 145.61 | 3.3563 | 347.21 | 0.56549 | 204.16 | 3.2441 | 445.38 | 0.63768 | 311.04 | 1.82 | 534.29 | 0.68751 | 318.28 | 4.0749 | 510.78 | 1.415
59.761 | 0.29342 | 220.6 | 0.060191 | 41.903 | 1.1593 | 189.49 | 0.090715 | 49.419 | 1.4548 | 221.48 | 0.10388 | 65.258 | 1.4005 | 247.24 | 0.13099 | 100.72 | 0.9056 | 341.84 | 0.11863 | 322.44 | 0.16511 | 596.41 | 0.089079 | 192.28 | 0.57398 | 545.63 | 0.11729 | 150.19 | 1.8073 | 306.72 | 0.48798 | 151.1 | 2.9798 | 372.39 | 0.49327 | 210.59 | 2.9442 | 463.1 | 0.59033 | 322.44 | 1.66 | 560.56 | 0.62364 | 326.99 | 3.6908 | 543.45 | 1.2191
64.932 | 0.24656 | 244.53 | 0.056281 | 43.352 | 1.0659 | 209.84 | 0.079593 | 51.953 | 1.2723 | 248.72 | 0.088476 | 68.879 | 1.2273 | 269.98 | 0.11462 | 107.06 | 0.78887 | 385.04 | 0.099794 | 355.29 | 0.13654 | 644.15 | 0.080955 | 210.17 | 0.4828 | 583.43 | 0.10635 | 155.39 | 1.6567 | 329.95 | 0.42411 | 157.74 | 2.6375 | 415.69 | 0.40187 | 218.1 | 2.6614 | 482.96 | 0.54303 | 333.93 | 1.5141 | 591.07 | 0.56231 | 335.27 | 3.3731 | 569.6 | 1.0921
71.261 | 0.20247 | 265.69 | 0.053623 | 45.438 | 0.95584 | 233.77 | 0.071707 | 54.399 | 1.133 | 273.79 | 0.078789 | 71.833 | 1.1072 | 295.11 | 0.10039 | 113.11 | 0.69617 | 422.14 | 0.087809 | 382.96 | 0.11764 | 709.05 | 0.073625 | 230.66 | 0.40165 | 624.49 | 0.096489 | 160.28 | 1.5263 | 354.58 | 0.36971 | 165.16 | 2.316 | 458.49 | 0.33538 | 224.51 | 2.4421 | 510.78 | 0.48886 | 347.56 | 1.3687 | 623.86 | 0.50596 | 345.48 | 3.0644 | 609.07 | 0.93479
78.598 | 0.1666 | 287.54 | 0.051486 | 47.815 | 0.85116 | 268.63 | 0.063794 | 56.96 | 1.0099 | 303.49 | 0.071446 | 74.84 | 1.0049 | 321.93 | 0.08913 | 121.55 | 0.59502 | 471.7 | 0.077267 | 412.79 | 0.10115 | 768.88 | 0.068417 | 249.37 | 0.34295 | 685.35 | 0.085054 | 166.49 | 1.3935 | 402.19 | 0.29358 | 172.59 | 2.05 | 525.28 | 0.26225 | 231.58 | 2.2185 | 542.9 | 0.43332 | 359.22 | 1.266 | 661.78 | 0.45223 | 358.14 | 2.7562 | 638.38 | 0.8415
87.825 | 0.1333 | 308.07 | 0.049855 | 50.671 | 0.74814 | 298.67 | 0.059057 | 59.88 | 0.89659 | 333.73 | 0.065886 | 79.547 | 0.87183 | 357.22 | 0.078432 | 129.59 | 0.52092 | 521.83 | 0.070174 | 449.41 | 0.085849 | 829.59 | 0.06432 | 275.6 | 0.28079 | 755.16 | 0.076472 | 173.11 | 1.2622 | 441.39 | 0.24871 | 178.92 | 1.8605 | 606.64 | 0.20388 | 239.35 | 2.0256 | 583.43 | 0.38027 | 370.9 | 1.1792 | 723.38 | 0.38708 | 370.16 | 2.4964 | 673.13 | 0.75092
96.965 | 0.10914 | 320.65 | 0.049 | 53.75 | 0.65892 | 330.74 | 0.055372 | 63.329 | 0.78887 | 368.83 | 0.061012 | 84.044 | 0.77093 | 390.08 | 0.072069 | 137.6 | 0.45787 | 569.83 | 0.065091 | 491.73 | 0.071492 | 897.79 | 0.060641 | 294.4 | 0.24557 | 822.98 | 0.070519 | 180.54 | 1.1478 | 485.38 | 0.21083 | 186.03 | 1.6851 | 659.8 | 0.17704 | 246.15 | 1.8754 | 618.89 | 0.34254 | 385.65 | 1.0713 | 805.88 | 0.31858 | 382.96 | 2.2633 | 713.32 | 0.66186
107.38 | 0.089174 | 321 | 0.045 | 57.705 | 0.56374 | 370.31 | 0.052021 | 67.38 | 0.68307 | 405.19 | 0.057239 | 90.138 | 0.65563 | 435 | 0.065565 | 145.96 | 0.40448 | 642.49 | 0.059565 | 551.11 | 0.056974 | 980.37 | 0.057276 | 319.24 | 0.20926 | 898.68 | 0.065432 | 189.41 | 1.0293 | 530.56 | 0.18133 | 193.43 | 1.5293 | 716.9 | 0.15445 | 256.71 | 1.6885 | 663.1 | 0.30223 | 399.39 | 0.98594 | 888.85 | 0.26771 | 399.79 | 2.0074 | 756.67 | 0.58509
119.03 | 0.072355 | 450 | 0.045 | 63.076 | 0.46712 | 403.97 | 0.049953 | 71.332 | 0.60401 | 447.8 | 0.053963 | 98.627 | 0.5384 | 475.49 | 0.061233 | 157.01 | 0.34709 | 703.69 | 0.05616 | 596.41 | 0.048744 | 1053.6 | 0.054841 | 340.68 | 0.18339 | 962.88 | 0.062048 | 201.33 | 0.89748 | 584.02 | 0.15493 | 203.35 | 1.3578 | 764.28 | 0.1395 | 269.6 | 1.4856 | 719.77 | 0.26058 | 419.44 | 0.88501 | 998.18 | 0.21888 | 414.86 | 1.8164 | 801.06 | 0.52002
132.73 | 0.058416 | 641.3 | 0.045 | 69.501 | 0.38054 | 422.99 | 0.049 | 74.989 | 0.54001 | 487.53 | 0.051649 | 107.27 | 0.44971 | 535.04 | 0.056542 | 166.39 | 0.30846 | 807.82 | 0.052034 | 644.15 | 0.041955 | 1151.6 | 0.052271 | 367.94 | 0.15721 | 1042 | 0.05868 | 213.35 | 0.78808 | 648.03 | 0.13134 | 211.65 | 1.2286 | 820.51 | 0.12481 | 282.01 | 1.3376 | 789.13 | 0.22185 | 445.83 | 0.77479 | 1102.1 | 0.18516 | 429.63 | 1.6468 | 866.04 | 0.44316
146.55 | 0.047779 | 642 | 0.043 | 74.392 | 0.33016 | 423 | 0.045 | 79.946 | 0.47135 | 526.02 | 0.049855 | 120.34 | 0.35199 | 577.87 | 0.054023 | 178.1 | 0.26816 | 873.36 | 0.050152 | 709.05 | 0.034625 | 1222.8 | 0.050747 | 397.39 | 0.13504 | 1120.9 | 0.056023 | 224.51 | 0.70669 | 708.35 | 0.11477 | 222.5 | 1.0973 | 901.38 | 0.10856 | 297.65 | 1.178 | 866.04 | 0.18898 | 473.87 | 0.67898 | 1196.2 | 0.162 | 441.83 | 1.5278 | 914.09 | 0.39803
162.44 | 0.038962 | 12500 | 0.043 | 79.15 | 0.28963 | 600 | 0.045 | 87.212 | 0.3937 | 548.04 | 0.049 | 132.2 | 0.29021 | 626.62 | 0.05184 | 191.97 | 0.23012 | 921.81 | 0.049 | 768.88 | 0.029417 | 1295.9 | 0.04945 | 430.49 | 0.11496 | 1197.4 | 0.053933 | 234.38 | 0.64522 | 778.94 | 0.099983 | 233.44 | 0.9889 | 954.26 | 0.10018 | 316.06 | 1.0293 | 994.19 | 0.15033 | 501.66 | 0.6016 | 1295.9 | 0.14261 | 458.49 | 1.3949 | 968.68 | 0.35611
177.39 | 0.032772 | 25000 | 0.043 | 84.213 | 0.2556 | 845.98 | 0.045 | 94.855 | 0.33149 | 549 | 0.045 | 143.07 | 0.24705 | 672.73 | 0.050107 | 210.68 | 0.19183 | 922 | 0.045 | 829.59 | 0.02532 | 1326 | 0.049 | 466.35 | 0.097865 | 1277.8 | 0.0521 | 242.97 | 0.5974 | 848.04 | 0.089013 | 244.43 | 0.89569 | 1016.3 | 0.0918 | 334.26 | 0.90923 | 1087.8 | 0.13033 | 534.29 | 0.52826 | 1423.6 | 0.12372 | 482.48 | 1.2298 | 1026.5 | 0.31731
201.01 | 0.025472 |  |  | 89.958 | 0.22287 | 846 | 0.043 | 101.83 | 0.28703 | 750 | 0.045 | 155.76 | 0.20864 | 708.64 | 0.049 | 235.65 | 0.15302 | 1500 | 0.045 | 897.79 | 0.021641 | 1327 | 0.045 | 498.17 | 0.085935 | 1343.4 | 0.050829 | 252.88 | 0.54872 | 926.98 | 0.079796 | 258.25 | 0.796 | 1073.8 | 0.085305 | 354.23 | 0.79919 | 1190.3 | 0.11394 | 560.56 | 0.47847 | 1519.2 | 0.11229 | 510.78 | 1.0723 | 1090 | 0.28303
220.6 | 0.021191 |  |  | 96.771 | 0.1924 | 12500 | 0.043 | 110.21 | 0.24435 | 1096.08 | 0.045 | 171.46 | 0.17236 | 709 | 0.045 | 266.23 | 0.12013 | 1843.62 | 0.045 | 980.37 | 0.018276 | 2000 | 0.045 | 545.63 | 0.071564 | 1396.8 | 0.049964 | 267.45 | 0.49009 | 1010.2 | 0.073384 | 270.95 | 0.71953 | 1127.7 | 0.080165 | 379.91 | 0.68512 | 1298.5 | 0.10013 | 591.07 | 0.42949 | 1632.6 | 0.10121 | 543.45 | 0.92389 | 1183.1 | 0.24301
244.53 | 0.017281 |  |  | 104.73 | 0.16494 | 25000 | 0.043 | 119.14 | 0.20926 | 1097 | 0.043 | 190.44 | 0.13943 | 1000 | 0.045 | 300.77 | 0.093746 | 1844 | 0.043 | 1053.6 | 0.015841 | 2652 | 0.045 | 583.43 | 0.062652 | 1436.5 | 0.049377 | 277.81 | 0.45196 | 1090 | 0.068506 | 285.7 | 0.64522 | 1202.2 | 0.075255 | 400.59 | 0.60947 | 1417.9 | 0.088747 | 623.86 | 0.38939 | 1786.3 | 0.089465 | 569.6 | 0.82848 | 1295.9 | 0.2071
265.69 | 0.014623 |  |  | 116.2 | 0.13277 |  |  | 130.24 | 0.17497 | 12500 | 0.043 | 207.13 | 0.11799 | 1417.28 | 0.045 | 341.84 | 0.072718 | 12500 | 0.043 | 1151.6 | 0.013271 | 2653 | 0.043 | 624.49 | 0.054794 | 1462.5 | 0.049 | 291.47 | 0.41018 | 1185.5 | 0.063968 | 300.35 | 0.58091 | 1265.1 | 0.071805 | 427.92 | 0.53091 | 1573.3 | 0.078197 | 661.78 | 0.34571 | 1942.9 | 0.080454 | 609.07 | 0.71166 | 1435 | 0.17381
287.54 | 0.012486 |  |  | 128.3 | 0.10946 |  |  | 141.65 | 0.14747 | 25000 | 0.043 | 225.96 | 0.099047 | 1418 | 0.043 | 385.04 | 0.057546 | 25000 | 0.043 | 1222.8 | 0.011747 | 12500 | 0.043 | 685.35 | 0.045403 | 1463 | 0.045 | 306.72 | 0.36893 | 1298.4 | 0.059792 | 312.6 | 0.53357 | 1328.7 | 0.068654 | 445.38 | 0.49058 | 1752.7 | 0.070677 | 723.38 | 0.29108 | 2083.8 | 0.075219 | 638.38 | 0.64072 | 1563.9 | 0.15086
308.07 | 0.010855 |  |  | 140.8 | 0.090794 |  |  | 156.23 | 0.12183 |  |  | 247.24 | 0.082318 | 12500 | 0.043 | 422.14 | 0.047588 |  |  | 1295.9 | 0.01045 | 25000 | 0.043 | 755.16 | 0.037472 | 2000 | 0.045 | 329.95 | 0.31977 | 1453.8 | 0.055686 | 328.63 | 0.4828 | 1394 | 0.065939 | 463.1 | 0.45106 | 1915.9 | 0.065485 | 805.88 | 0.23571 | 2221.5 | 0.070868 | 673.13 | 0.57055 | 1709.5 | 0.13097
320.65 | 0.01 |  |  | 156.86 | 0.072791 |  |  | 171.29 | 0.10155 |  |  | 269.98 | 0.06931 | 25000 | 0.043 | 471.7 | 0.038267 |  |  | 1326 | 0.01 |  |  | 822.98 | 0.031519 | 2925 | 0.045 | 354.58 | 0.27578 | 1559.2 | 0.053463 | 347.21 | 0.43424 | 1496.6 | 0.062443 | 482.96 | 0.41347 | 2125.8 | 0.060641 | 888.85 | 0.19395 | 2365.9 | 0.067039 | 713.32 | 0.5025 | 1861.1 | 0.11513
|  |  |  | 173.53 | 0.059895 |  |  | 191.01 | 0.081499 |  |  | 295.11 | 0.057893 |  |  | 521.83 | 0.031174 | [6 empty] | 898.68 | 0.026432 | 2926 | 0.043 | 402.19 | 0.21413 | 1649 | 0.051956 | 372.39 | 0.37638 | 1576.4 | 0.060064 | 510.78 | 0.37077 | 2296 | 0.057571 | 998.18 | 0.15394 | 2542.6 | 0.063376 | 756.67 | 0.4408 | 2067.2 | 0.098996
|  |  |  | 189.49 | 0.050128 |  |  | 221.48 | 0.060739 |  |  | 321.93 | 0.048647 |  |  | 569.83 | 0.026091 | [6 empty] | 962.88 | 0.023048 | 12500 | 0.043 | 441.39 | 0.17797 | 1724.9 | 0.050829 | 415.69 | 0.30145 | 1685.7 | 0.057441 | 542.9 | 0.33016 | 2464.9 | 0.055112 | 1102.1 | 0.1268 | 2787.6 | 0.059299 | 801.06 | 0.39057 | 2246.1 | 0.088283
|  |  |  | 209.84 | 0.040593 |  |  | 248.72 | 0.048308 |  |  | 357.22 | 0.039432 |  |  | 642.49 | 0.020565 | [6 empty] | 1042 | 0.01968 | 25000 | 0.043 | 485.38 | 0.14761 | 1798.9 | 0.04992 | 458.49 | 0.24804 | 1781 | 0.05557 | 583.43 | 0.28589 | 2659.6 | 0.052868 | 1196.2 | 0.10848 | 3025.8 | 0.056194 | 866.04 | 0.33182 | 2509.7 | 0.07769
|  |  |  | 233.77 | 0.032707 |  |  | 273.79 | 0.039789 |  |  | 390.08 | 0.033069 |  |  | 703.69 | 0.01716 | [6 empty] | 1120.9 | 0.017023 |  |  | 530.56 | 0.12367 | 1850 | 0.049325 | 525.28 | 0.18878 | 1893 | 0.053652 | 618.89 | 0.25356 | 2762.6 | 0.051827 | 1295.9 | 0.092628 | 3258.2 | 0.053903 | 914.09 | 0.29489 | 2743.3 | 0.071414
|  |  |  | 268.63 | 0.024794 |  |  | 303.49 | 0.032446 |  |  | 435 | 0.026565 |  |  | 807.82 | 0.013034 | [6 empty] | 1197.4 | 0.014933 |  |  | 584.02 | 0.10206 | 1877.9 | 0.049 | 606.64 | 0.14197 | 1984.1 | 0.052378 | 663.1 | 0.22132 | 2875.3 | 0.050889 | 1423.6 | 0.076906 | 3543.7 | 0.051599 | 968.68 | 0.26076 | 3034.9 | 0.065406
|  |  |  | 298.67 | 0.020057 |  |  | 333.73 | 0.026886 |  |  | 475.49 | 0.022233 |  |  | 873.36 | 0.011152 | [6 empty] | 1277.8 | 0.0131 |  |  | 648.03 | 0.082896 | 1878 | 0.045 | 659.8 | 0.12013 | 2061 | 0.051386 | 719.77 | 0.18784 | 2980.7 | 0.050041 | 1519.2 | 0.067599 | 3800.6 | 0.049942 | 1026.5 | 0.23058 | 3261.4 | 0.06191
|  |  |  | 330.74 | 0.016372 |  |  | 368.83 | 0.022012 |  |  | 535.04 | 0.017542 |  |  | 921.81 | 0.01 | [6 empty] | 1343.4 | 0.011829 |  |  | 708.35 | 0.069588 | 2500 | 0.045 | 716.9 | 0.10155 | 2138.7 | 0.050514 | 789.13 | 0.15612 | 3090 | 0.049336 | 1632.6 | 0.058533 | 3916.4 | 0.049325 | 1090 | 0.2043 | 3536.6 | 0.058503
|  |  |  | 370.31 | 0.013021 |  |  | 405.19 | 0.018239 |  |  | 577.87 | 0.015023 | [10 empty] | 1396.8 | 0.010964 |  |  | 778.94 | 0.057661 | 3755.8 | 0.045 | 764.28 | 0.089442 | 2208.2 | 0.049811 | 866.04 | 0.12936 | 3133.6 | 0.049 | 1786.3 | 0.049136 | 3967.7 | 0.049 | 1183.1 | 0.17271 | 3789.3 | 0.056023
|  |  |  | 403.97 | 0.010953 |  |  | 447.8 | 0.014963 |  |  | 626.62 | 0.01284 | [10 empty] | 1436.5 | 0.010377 |  |  | 848.04 | 0.048696 | 3756 | 0.043 | 820.51 | 0.077913 | 2261.8 | 0.049284 | 994.19 | 0.098651 | 3134 | 0.045 | 1942.9 | 0.041454 | 3968 | 0.045 | 1295.9 | 0.14382 | 4142 | 0.053248
|  |  |  | 422.99 | 0.01 |  |  | 487.53 | 0.012649 |  |  | 672.73 | 0.011107 | [10 empty] | 1462.5 | 0.01 |  |  | 926.98 | 0.040796 | 12500 | 0.043 | 901.38 | 0.064689 | 2289.1 | 0.049 | 1087.8 | 0.082154 | 4500 | 0.045 | 2083.8 | 0.036219 | 6500 | 0.045 | 1435 | 0.11717 | 4354.3 | 0.051879
[8 empty] | 526.02 | 0.010855 |  |  | 708.64 | 0.01 | [14 empty] | 1010.2 | 0.034384 | 25000 | 0.043 | 954.26 | 0.057777 | 2290 | 0.045 | 1190.3 | 0.068758 | 6267.2 | 0.045 | 2221.5 | 0.031868 | 7935.4 | 0.045 | 1563.9 | 0.098651 | 4573 | 0.050688
[8 empty] | 548.04 | 0.01 | [18 empty] | 1090 | 0.029506 |  |  | 1016.3 | 0.050734 | 3500 | 0.045 | 1298.5 | 0.057546 | 6268 | 0.043 | 2365.9 | 0.028039 | 7936 | 0.043 | 1709.5 | 0.082648 | 4731.2 | 0.049931
[28 empty] | 1185.5 | 0.024968 |  |  | 1073.8 | 0.045403 | 4578.2 | 0.045 | 1417.9 | 0.048308 | 12500 | 0.043 | 2542.6 | 0.024376 | 12500 | 0.043 | 1861.1 | 0.069937 | 4855.8 | 0.049377
[28 empty] | 1298.4 | 0.020792 |  |  | 1127.7 | 0.041165 | 4579 | 0.043 | 1573.3 | 0.039197 | 25000 | 0.043 | 2787.6 | 0.020299 | 25000 | 0.043 | 2067.2 | 0.056917 | 4929.2 | 0.049
[28 empty] | 1453.8 | 0.016686 |  |  | 1202.2 | 0.036255 | 12500 | 0.043 | 1752.7 | 0.031677 |  |  | 3025.8 | 0.017194 |  |  | 2246.1 | 0.048019 | 4930 | 0.045
[28 empty] | 1559.2 | 0.014463 |  |  | 1265.1 | 0.032805 | 25000 | 0.043 | 1915.9 | 0.026485 |  |  | 3258.2 | 0.014903 |  |  | 2509.7 | 0.03869 | 7500 | 0.045
[28 empty] | 1649 | 0.012956 |  |  | 1328.7 | 0.029654 |  |  | 2125.8 | 0.021641 |  |  | 3543.7 | 0.012599 |  |  | 2743.3 | 0.032414 | 9858.4 | 0.045
[28 empty] | 1724.9 | 0.011829 |  |  | 1394 | 0.026939 |  |  | 2296 | 0.018571 |  |  | 3800.6 | 0.010942 |  |  | 3034.9 | 0.026406 | 9859 | 0.043
[28 empty] | 1798.9 | 0.01092 |  |  | 1496.6 | 0.023443 |  |  | 2464.9 | 0.016112 |  |  | 3916.4 | 0.010325 |  |  | 3261.4 | 0.02291 | 12500 | 0.043
[28 empty] | 1850 | 0.010325 |  |  | 1576.4 | 0.021064 |  |  | 2659.6 | 0.013868 |  |  | 3967.7 | 0.01 |  |  | 3536.6 | 0.019503 | 25000 | 0.043
[28 empty] | 1877.9 | 0.01 |  |  | 1685.7 | 0.018441 |  |  | 2762.6 | 0.012827 | [6 empty] | 3789.3 | 0.017023
[32 empty] | 1781 | 0.01657 |  |  | 2875.3 | 0.011889 | [6 empty] | 4142 | 0.014248
[32 empty] | 1893 | 0.014652 |  |  | 2980.7 | 0.011041 | [6 empty] | 4354.3 | 0.012879
[32 empty] | 1984.1 | 0.013378 |  |  | 3090 | 0.010336 | [6 empty] | 4573 | 0.011688
[32 empty] | 2061 | 0.012386 |  |  | 3133.6 | 0.01 | [6 empty] | 4731.2 | 0.010931
[32 empty] | 2138.7 | 0.011514 | [10 empty] | 4855.8 | 0.010377
[32 empty] | 2208.2 | 0.010811 | [10 empty] | 4929.2 | 0.01
[32 empty] | 2261.8 | 0.010284
[32 empty] | 2289.1 | 0.01

## 60 Hz, 1320-1 CT Ratio
S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0
S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018
60 Hz, 1320:1 CT Ratio | [11 empty] | 60 Hz, 1320:1 CT Ratio | [11 empty] | 60 Hz, 1320:1 CT Ratio | [11 empty] | 60 Hz, 1320:1 CT Ratio | [11 empty] | 60 Hz, 1320:1 CT Ratio | [11 empty] | 60 Hz, 1320:1 CT Ratio
Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information.
8K |  |  |  | 10K |  |  |  | 12K |  |  |  | 15K |  |  |  | 20K |  |  |  | 25K |  |  |  | 30K |  |  |  | 40K |  |  |  | 50K |  |  |  | 65K |  |  |  | 80K |  |  |  | 100K |  |  |  | 125K |  |  |  | 150K |  |  |  | 175K |  |  |  | 200K
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
32.896 | 1000 | 39.109 | 1000 | 42.451 | 1000 | 48.684 | 1000 | 49.597 | 1000 | 57.165 | 1000 | 59.915 | 1000 | 67.893 | 1000 | 79.594 | 1000 | 89.205 | 1000 | 97.997 | 1000 | 109.06 | 1000 | 128.37 | 1000 | 143.3 | 1000 | 159.32 | 1000 | 178.03 | 1000 | 195.18 | 1000 | 217.44 | 1000 | 274.55 | 1000 | 312.55 | 1000 | 329.65 | 1000 | 378.1 | 1000 | 401.85 | 1000 | 448.4 | 1000 | 479.75 | 1000 | 570 | 1000 | 329.65 | 1000 | 378.1 | 1000 | 401.85 | 1000 | 448.4 | 1000 | 479.75 | 1000 | 570 | 1000
32.896 | 300.92 | 39.109 | 217.099 | 42.451 | 303.64 | 48.684 | 252.399 | 49.597 | 602.96 | 57.165 | 20.317 | 59.915 | 608.41 | 67.893 | 81.774 | 79.594 | 609.02 | 89.205 | 452.689 | 97.997 | 602.36 | 109.06 | 557.549 | 128.37 | 601.76 | 143.3 | 274.409 | 159.32 | 605.98 | 178.03 | 538.399 | 195.18 | 601.15 | 217.44 | 569.259 | 274.55 | 600 | 312.55 | 170.109 | 329.65 | 600 | 378.1 | 164.259 | 401.85 | 600 | 448.4 | 559.789 | 479.75 | 600 | 570 | 162.329 | 329.65 | 600 | 378.1 | 164.259 | 401.85 | 600 | 448.4 | 559.789 | 479.75 | 600 | 570 | 162.329
32.962 | 270.93 | 39.899 | 64.193 | 42.621 | 261.09 | 49.519 | 118.829 | 49.996 | 26.492 | 58.67 | 14.728 | 60.156 | 161.23 | 69.612 | 40.642 | 79.753 | 578.16 | 90.462 | 246.119 | 98.095 | 568.98 | 110.38 | 322.719 | 128.5 | 569.55 | 145.03 | 129.799 | 159.96 | 559.39 | 181.08 | 308.659 | 195.96 | 553.83 | 220.29 | 351.899 | 275.5 | 300 | 340.1 | 64.209 | 332.5 | 300 | 408.5 | 66.843 | 413.25 | 300 | 482.6 | 150.709 | 494 | 300 | 625.1 | 64.79 | 332.5 | 300 | 408.5 | 66.843 | 413.25 | 300 | 482.6 | 150.709 | 494 | 300 | 625.1 | 64.79
33.061 | 223.15 | 40.705 | 35.116 | 42.835 | 212.91 | 50.62 | 44.571 | 50.599 | 22.04 | 60.336 | 11.532 | 60.336 | 117.2 | 71.517 | 25.39 | 79.913 | 513.81 | 92.752 | 96.975 | 98.389 | 488.26 | 112.05 | 102.719 | 128.5 | 461.21 | 146.78 | 94.061 | 160.44 | 498.62 | 184.37 | 184.099 | 196.75 | 446.68 | 222.95 | 241.709 | 277.4 | 200 | 365.75 | 36.992 | 334.4 | 200 | 446.5 | 35.771 | 422.75 | 200 | 517.75 | 72.508 | 503.5 | 200 | 682.1 | 34.271 | 334.4 | 200 | 446.5 | 35.771 | 422.75 | 200 | 517.75 | 72.508 | 503.5 | 200 | 682.1 | 34.271
33.16 | 181.43 | 41.652 | 22.544 | 43.049 | 167.81 | 51.643 | 27.827 | 51.415 | 18.063 | 62.298 | 9.75 | 60.821 | 88.31 | 73.474 | 18.522 | 80.313 | 422.36 | 94.532 | 61.887 | 98.685 | 424.48 | 113.63 | 66.198 | 128.5 | 359.55 | 148.7 | 69.508 | 161.41 | 415.24 | 187.72 | 113.959 | 197.93 | 362.07 | 225.64 | 185.449 | 287.85 | 100 | 427.5 | 15.999 | 348.65 | 100 | 515.85 | 16.613 | 448.4 | 100 | 555.75 | 39.667 | 530.1 | 100 | 798 | 15.955 | 348.65 | 100 | 515.85 | 16.613 | 448.4 | 100 | 555.75 | 39.667 | 530.1 | 100 | 798 | 15.955
33.226 | 149.58 | 42.664 | 16.085 | 43.222 | 135.08 | 52.844 | 18.748 | 52.349 | 15.224 | 64.582 | 8.3557 | 61.248 | 67.684 | 75.787 | 13.748 | 80.716 | 336.25 | 96.249 | 41.64 | 99.081 | 347.88 | 115.11 | 46.687 | 128.89 | 278.62 | 150.8 | 50.542 | 162.54 | 325.99 | 191.7 | 79.514 | 198.93 | 299.12 | 228.82 | 141.939 | 312.55 | 50 | 513 | 7.4923 | 378.1 | 50 | 617.5 | 7.5333 | 482.6 | 50 | 647.9 | 16.126 | 570 | 50 | 950 | 7.6302 | 378.1 | 50 | 617.5 | 7.5333 | 448.4 | 100 | 647.9 | 16.126 | 570 | 50 | 950 | 7.6302
33.36 | 119.68 | 43.875 | 11.89 | 43.526 | 107.97 | 54.182 | 13.576 | 53.353 | 13.129 | 66.949 | 7.2326 | 61.74 | 54.209 | 77.706 | 11.372 | 81.283 | 255.66 | 98.193 | 29.509 | 99.478 | 282.55 | 116.86 | 33.143 | 129.01 | 216.34 | 152.77 | 38.814 | 163.68 | 258.75 | 195.96 | 54.625 | 200.12 | 251.6 | 232.04 | 112.819 | 340.1 | 30 | 595.65 | 4.3303 | 408.5 | 30 | 717.25 | 4.3265 | 517.75 | 30 | 779 | 7.4607 | 625.1 | 30 | 1102 | 4.3403 | 378.1 | 50 | 717.25 | 4.3265 | 482.6 | 50 | 779 | 7.4607 | 570 | 50 | 1102 | 4.3403
33.493 | 99.768 | 45.076 | 9.4913 | 43.831 | 85.528 | 55.498 | 10.952 | 54.16 | 11.645 | 69.403 | 6.2399 | 62.298 | 43.417 | 80.153 | 9.2222 | 81.69 | 201.51 | 100.08 | 23.27 | 99.677 | 223.6 | 118.74 | 24.695 | 129.4 | 170.69 | 155.23 | 31.524 | 164.83 | 207.03 | 199.92 | 40.811 | 201.33 | 209.11 | 235.32 | 92.087 | 365.75 | 20 | 674.5 | 2.8491 | 446.5 | 20 | 807.5 | 2.8969 | 555.75 | 20 | 902.5 | 4.3537 | 682.1 | 20 | 1244.5 | 2.8708 | 408.5 | 30 | 807.5 | 2.8969 | 517.75 | 30 | 902.5 | 4.3537 | 625.1 | 30 | 1244.5 | 2.8708
33.594 | 81.683 | 46.263 | 7.721 | 43.963 | 69.467 | 56.903 | 8.6711 | 55.42 | 10.205 | 73.401 | 5.2035 | 62.924 | 35.299 | 82.346 | 7.8024 | 82.182 | 155.07 | 102.4 | 18.068 | 99.976 | 173.79 | 120.53 | 20.444 | 129.92 | 141.01 | 158.21 | 24.942 | 166.16 | 159.31 | 203.76 | 30.821 | 203.35 | 178.19 | 238.63 | 76.116 | 427.5 | 10 | 855 | 1.3897 | 515.85 | 10 | 1026 | 1.3856 | 647.9 | 10 | 1035.5 | 2.7579 | 798 | 10 | 1577 | 1.3903 | 446.5 | 20 | 1026 | 1.3856 | 555.75 | 20 | 1035.5 | 2.7579 | 682.1 | 20 | 1577 | 1.3903
33.762 | 67.549 | 47.959 | 6.1808 | 44.272 | 55.249 | 58.46 | 7.2215 | 57.165 | 8.8804 | 77.396 | 4.4028 | 63.493 | 30.412 | 84.769 | 6.6148 | 82.594 | 126.58 | 103.95 | 15.174 | 100.28 | 127.47 | 122.85 | 15.797 | 130.97 | 115.45 | 160.44 | 21.016 | 167.99 | 124.19 | 207.67 | 25.129 | 205.39 | 146.77 | 243.7 | 59.009 | 513 | 5 | 1092.5 | 0.70254 | 617.5 | 5 | 1320.5 | 0.69682 | 779 | 5 | 1301.5 | 1.4053 | 950 | 5 | 2042.5 | 0.69212 | 515.85 | 10 | 1320.5 | 0.69682 | 647.9 | 10 | 1301.5 | 1.4053 | 798 | 10 | 2042.5 | 0.69212
33.932 | 55.693 | 49.767 | 5.074 | 44.538 | 45.597 | 60.18 | 6.0812 | 58.67 | 7.9236 | 81.69 | 3.7816 | 64.067 | 26.466 | 87.438 | 5.7058 | 83.091 | 104.88 | 106.58 | 12.08 | 100.68 | 105.94 | 125.08 | 13.473 | 131.75 | 98.087 | 163.68 | 17.003 | 170.36 | 94.903 | 211.65 | 20.167 | 207.46 | 122.1 | 247.63 | 50.071 | 595.65 | 3 | 1349 | 0.41622 | 717.25 | 3 | 1615 | 0.42094 | 902.5 | 3 | 1681.5 | 0.69394 | 1102 | 3 | 2508 | 0.41891 | 617.5 | 5 | 1615 | 0.42094 | 779 | 5 | 1681.5 | 0.69394 | 950 | 5 | 2508 | 0.41891
34.17 | 45.917 | 51.901 | 4.1153 | 44.941 | 37.146 | 62.075 | 5.1133 | 60.336 | 7.0628 | 84.854 | 3.4244 | 64.906 | 22.507 | 90.734 | 4.9085 | 83.675 | 85.871 | 108.85 | 10.167 | 101.18 | 86.995 | 127.22 | 11.449 | 132.94 | 76.39 | 166.82 | 14.504 | 172.59 | 75.554 | 215.71 | 16.501 | 209.96 | 101.58 | 251.62 | 41.395 | 674.5 | 2 | 1615 | 0.28258 | 807.5 | 2 | 1947.5 | 0.28027 | 1035.5 | 2 | 2061.5 | 0.4197 | 1244.5 | 2 | 2973.5 | 0.28604 | 717.25 | 3 | 1947.5 | 0.28027 | 902.5 | 3 | 2061.5 | 0.4197 | 1102 | 3 | 2973.5 | 0.28604
34.376 | 38.584 | 54.02 | 3.4466 | 45.347 | 29.721 | 64.351 | 4.3759 | 62.298 | 6.2641 | 90.011 | 2.9333 | 65.492 | 19.942 | 94.248 | 4.1819 | 84.6 | 67.145 | 111.27 | 8.5035 | 101.49 | 74.877 | 129.4 | 10.077 | 134.01 | 64.062 | 170.36 | 12.279 | 175.2 | 59.196 | 221.17 | 13.576 | 212.29 | 88.752 | 255.94 | 34.89 | 855 | 1 | 2194.5 | 0.15589 | 1026 | 1 | 2669.5 | 0.15506 | 1301.5 | 1 | 2479.5 | 0.28107 | 1577 | 1 | 4085 | 0.15485 | 807.5 | 2 | 2669.5 | 0.15506 | 1035.5 | 2 | 2479.5 | 0.28107 | 1244.5 | 2 | 4085 | 0.15485
34.756 | 32.683 | 56.903 | 2.8497 | 45.849 | 23.923 | 66.709 | 3.8261 | 64.582 | 5.5392 | 95.196 | 2.5428 | 66.349 | 17.705 | 98.291 | 3.6304 | 85.365 | 52.712 | 113.86 | 7.2896 | 102.3 | 61.121 | 131.62 | 8.9125 | 135.09 | 53.455 | 173.8 | 10.715 | 178.03 | 45.872 | 225.86 | 11.434 | 214.63 | 76.619 | 260.85 | 29 | 1092.5 | 0.5 | 3040 | 0.091559 | 1320.5 | 0.5 | 3676.5 | 0.091815 | 1681.5 | 0.5 | 3391.5 | 0.15526 | 2042.5 | 0.5 | 5633.5 | 0.091755 | 1026 | 1 | 3676.5 | 0.091815 | 1301.5 | 1 | 3391.5 | 0.15526 | 1577 | 1 | 5633.5 | 0.091755
35 | 28.555 | 59.582 | 2.4603 | 46.449 | 20.102 | 69.71 | 3.2546 | 66.949 | 4.9424 | 99.976 | 2.2706 | 67.893 | 14.152 | 102.82 | 3.1778 | 86.395 | 42.985 | 117.09 | 6.1416 | 102.81 | 51.876 | 134.15 | 7.6762 | 136.86 | 40.766 | 177.85 | 9.3575 | 181.08 | 34.843 | 229.97 | 9.9804 | 217.44 | 64.447 | 265.85 | 23.686 | 1349 | 0.3 | 3895 | 0.069 | 1615 | 0.3 | 4655 | 0.069 | 2061.5 | 0.3 | 4702.5 | 0.09152 | 2508 | 0.3 | 7172.5 | 0.069 | 1320.5 | 0.5 | 4655 | 0.066685 | 1681.5 | 0.5 | 4702.5 | 0.09152 | 2042.5 | 0.5 | 7172.5 | 0.066489
35.387 | 23.923 | 62.636 | 2.1327 | 47.151 | 16.691 | 72.919 | 2.8399 | 69.403 | 4.4187 | 106.26 | 1.9623 | 69.612 | 11.668 | 107.98 | 2.7653 | 87.089 | 36.739 | 122.11 | 4.9277 | 103.64 | 42.728 | 136.86 | 6.8372 | 138.51 | 34.29 | 181.8 | 8.1299 | 184.37 | 28.47 | 234.38 | 8.6768 | 220.29 | 56.252 | 270.95 | 19.936 | 1615 | 0.2 | 4655 | 0.059 | 1947.5 | 0.2 | 5605 | 0.059 | 2479.5 | 0.2 | 5937.5 | 0.069 | 2973.5 | 0.2 | 8645 | 0.059 | 1615 | 0.3 | 5605 | 0.055 | 2061.5 | 0.3 | 5937.5 | 0.066788 | 2508 | 0.3 | 8645 | 0.055
35.85 | 20.244 | 65.258 | 1.8977 | 47.911 | 14.095 | 76.428 | 2.4776 | 73.401 | 3.7691 | 111.94 | 1.7494 | 71.517 | 9.6296 | 113.17 | 2.4305 | 88.229 | 29.99 | 126.97 | 4.1405 | 104.47 | 35.796 | 140.74 | 5.8794 | 140.18 | 29.161 | 186.41 | 7.0139 | 187.72 | 22.756 | 240.07 | 7.3528 | 222.95 | 48.417 | 277.25 | 16.479 | 2194.5 | 0.1 | 6460 | 0.049 | 2669.5 | 0.1 | 7695 | 0.049 | 3391.5 | 0.1 | 7125 | 0.059 | 4085 | 0.1 | 11970 | 0.049 | 1947.5 | 0.2 | 7695 | 0.045 | 2479.5 | 0.2 | 7125 | 0.055 | 2973.5 | 0.2 | 11970 | 0.045
36.392 | 16.909 | 68.879 | 1.6454 | 48.684 | 12.156 | 80.668 | 2.1306 | 77.396 | 3.2539 | 119.45 | 1.5102 | 73.474 | 8.1079 | 118.86 | 2.1502 | 89.205 | 25.479 | 131.62 | 3.6373 | 105.63 | 29.573 | 145.61 | 4.9607 | 141.73 | 25.942 | 190.55 | 6.2698 | 191.7 | 18.135 | 244.19 | 6.7221 | 225.64 | 42.813 | 282.85 | 14.192 | 3040 | 0.05 | 6461 | 0.045 | 3676.5 | 0.05 | 7696 | 0.045 | 4702.5 | 0.05 | 9880 | 0.049 | 5633.5 | 0.05 | 11971 | 0.045 | 2669.5 | 0.1 | 10500 | 0.045 | 3391.5 | 0.1 | 9880 | 0.045 | 4085 | 0.1 | 16000 | 0.045
36.942 | 14.51 | 71.833 | 1.4726 | 49.519 | 10.515 | 84.974 | 1.8333 | 81.69 | 2.8316 | 128.12 | 1.3035 | 75.787 | 6.7791 | 124.58 | 1.9103 | 90.462 | 21.176 | 136.72 | 3.2281 | 106.58 | 25.326 | 151.1 | 4.2563 | 143.3 | 22.328 | 196.75 | 5.4576 | 195.96 | 15.133 | 252.38 | 5.5737 | 228.82 | 37.034 | 287.99 | 12.381 | 3895 | 0.03 | 9000 | 0.045 | 4655 | 0.03 | 12500 | 0.045 | 5937.5 | 0.03 | 9881 | 0.045 | 7172.5 | 0.03 | 15000 | 0.045 | 3676.5 | 0.05 | 15390 | 0.045 | 4702.5 | 0.05 | 15000 | 0.045 | 5633.5 | 0.05 | 23940 | 0.045
37.5 | 12.589 | 74.84 | 1.3261 | 50.62 | 8.916 | 88.885 | 1.6339 | 84.854 | 2.5724 | 137.13 | 1.1333 | 77.706 | 5.9706 | 132.15 | 1.6489 | 92.752 | 16.23 | 141.16 | 2.924 | 107.66 | 21.908 | 157.74 | 3.6806 | 145.03 | 19.665 | 204.16 | 4.6521 | 199.92 | 12.729 | 258.51 | 4.8869 | 232.04 | 32.068 | 292.93 | 10.889 | 4655 | 0.02 | 12920 | 0.045 | 5605 | 0.02 | 15390 | 0.045 | 7125 | 0.02 | 15000 | 0.045 | 8645 | 0.02 | 23940 | 0.045 | 4655 | 0.03 | 15391 | 0.043 | 5937.5 | 0.03 | 19760 | 0.045 | 7172.5 | 0.03 | 23941 | 0.043
38.029 | 11.267 | 79.547 | 1.1487 | 51.643 | 7.79 | 94.57 | 1.3935 | 90.011 | 2.2341 | 146.93 | 0.98973 | 80.153 | 5.2218 | 139.9 | 1.449 | 94.532 | 13.368 | 145.9 | 2.6611 | 109.06 | 18.706 | 165.16 | 3.1874 | 146.78 | 17.424 | 210.59 | 4.1701 | 203.76 | 10.988 | 269.06 | 4.0808 | 235.32 | 27.711 | 299.44 | 9.4549 | 6460 | 0.01 | 12921 | 0.043 | 7695 | 0.01 | 15391 | 0.043 | 9880 | 0.01 | 19760 | 0.045 | 11970 | 0.01 | 23941 | 0.043 | 5605 | 0.02 | 25000 | 0.043 | 7125 | 0.02 | 19761 | 0.043 | 8645 | 0.02 | 25000 | 0.043
38.565 | 10.164 | 84.044 | 1.0097 | 52.844 | 6.7927 | 100.72 | 1.1932 | 95.196 | 1.9539 | 159.64 | 0.8391 | 82.346 | 4.6499 | 149 | 1.2571 | 96.249 | 11.38 | 150.19 | 2.4379 | 110.38 | 15.972 | 172.59 | 2.7859 | 148.7 | 15.438 | 218.1 | 3.6997 | 207.67 | 9.4863 | 277.25 | 3.5902 | 238.63 | 24.163 | 305.8 | 8.3741 |  |  | 17500 | 0.043 |  |  | 20000 | 0.043 |  |  | 19761 | 0.043 |  |  | 25000 | 0.043 | 7695 | 0.01 |  |  | 9880 | 0.01 | 25000 | 0.043 | 11970 | 0.01
39.109 | 9.1234 | 90.138 | 0.86265 | 54.182 | 5.9289 | 107.06 | 1.0357 | 99.976 | 1.7504 | 174.85 | 0.7064 | 84.769 | 4.1614 | 157.74 | 1.1116 | 98.193 | 9.8143 | 155.39 | 2.2225 | 112.05 | 13.913 | 178.92 | 2.5199 | 150.8 | 13.969 | 224.51 | 3.3655 | 211.65 | 8.3549 | 289.44 | 3.069 | 243.7 | 20.002 | 312.29 | 7.3855 |  |  | 25000 | 0.043 |  |  | 25000 | 0.043 |  |  | 22500 | 0.043
39.899 | 8.0433 | 98.627 | 0.71098 | 55.498 | 5.2218 | 113.11 | 0.91302 | 106.26 | 1.5187 | 193.24 | 0.58568 | 87.438 | 3.7279 | 171.56 | 0.93136 | 100.08 | 8.5066 | 160.28 | 2.0443 | 113.63 | 12.023 | 186.03 | 2.2621 | 152.77 | 12.526 | 231.58 | 3.0773 | 215.71 | 7.3879 | 300.64 | 2.7375 | 247.63 | 17.354 | 318.28 | 6.7235 | [10 empty] | 25000 | 0.043
40.705 | 7.1552 | 107.27 | 0.59403 | 56.903 | 4.6313 | 121.55 | 0.78086 | 111.94 | 1.3551 | 219.63 | 0.462 | 90.734 | 3.3262 | 192.28 | 0.73827 | 102.4 | 7.2852 | 166.49 | 1.8454 | 115.11 | 10.814 | 193.43 | 2.034 | 155.23 | 11.166 | 239.35 | 2.7848 | 221.17 | 6.4292 | 311.04 | 2.4623 | 251.62 | 15.285 | 326.99 | 5.8072
41.652 | 6.3525 | 120.34 | 0.46957 | 58.46 | 4.1489 | 129.59 | 0.68114 | 119.45 | 1.1816 | 238.16 | 0.39836 | 94.248 | 2.9708 | 210.17 | 0.62381 | 103.95 | 6.5133 | 173.11 | 1.6747 | 116.86 | 9.6296 | 203.35 | 1.7887 | 158.21 | 9.9428 | 246.15 | 2.5726 | 225.86 | 5.6908 | 322.44 | 2.2275 | 255.94 | 13.354 | 335.27 | 5.175
42.664 | 5.5892 | 132.2 | 0.39091 | 60.18 | 3.6945 | 137.6 | 0.60104 | 128.12 | 1.0252 | 260.32 | 0.33947 | 98.291 | 2.6349 | 230.66 | 0.52287 | 106.58 | 5.7136 | 180.54 | 1.5062 | 118.74 | 8.5749 | 211.65 | 1.6193 | 160.44 | 8.9338 | 256.71 | 2.2859 | 229.97 | 5.1031 | 333.93 | 2.0323 | 260.85 | 11.552 | 345.48 | 4.5683
43.875 | 4.9177 | 143.07 | 0.33549 | 62.075 | 3.3296 | 145.96 | 0.53504 | 137.13 | 0.88767 | 282.57 | 0.29318 | 102.82 | 2.3463 | 249.37 | 0.4524 | 108.85 | 5.0827 | 189.41 | 1.3473 | 120.53 | 7.7125 | 222.5 | 1.4377 | 163.68 | 7.9633 | 269.6 | 1.9838 | 234.38 | 4.636 | 347.56 | 1.8228 | 265.85 | 10.154 | 358.14 | 3.9367
45.076 | 4.3529 | 155.76 | 0.28691 | 64.351 | 2.9768 | 157.01 | 0.46198 | 146.93 | 0.77402 | 303.36 | 0.25848 | 107.98 | 2.0623 | 275.6 | 0.37606 | 111.27 | 4.5533 | 201.33 | 1.1674 | 122.85 | 6.8953 | 233.44 | 1.2887 | 166.82 | 7.1624 | 282.01 | 1.7669 | 240.07 | 4.1822 | 359.22 | 1.6781 | 270.95 | 9.0507 | 370.16 | 3.5091
46.263 | 3.8878 | 171.46 | 0.24154 | 66.709 | 2.6747 | 166.39 | 0.41258 | 159.64 | 0.65892 | 322.44 | 0.23267 | 113.17 | 1.8255 | 294.4 | 0.33256 | 113.86 | 4.1614 | 213.35 | 1.0272 | 125.08 | 6.1709 | 244.43 | 1.1577 | 170.36 | 6.4163 | 297.65 | 1.5511 | 244.19 | 3.8299 | 370.9 | 1.5543 | 277.25 | 7.8605 | 382.96 | 3.1337
47.959 | 3.431 | 190.44 | 0.20123 | 69.71 | 2.3557 | 178.1 | 0.36173 | 174.85 | 0.55202 | 355.29 | 0.19734 | 118.86 | 1.6223 | 319.24 | 0.28735 | 117.09 | 3.7428 | 224.51 | 0.91935 | 127.22 | 5.6173 | 258.25 | 1.0278 | 173.8 | 5.8348 | 316.06 | 1.3403 | 252.38 | 3.4104 | 385.65 | 1.4089 | 282.85 | 7.1053 | 399.79 | 2.7486
49.767 | 3.0127 | 207.13 | 0.17475 | 72.919 | 2.0665 | 191.97 | 0.31456 | 193.24 | 0.45241 | 382.96 | 0.17379 | 124.58 | 1.4548 | 340.68 | 0.2554 | 122.11 | 3.2734 | 234.38 | 0.84006 | 129.4 | 5.1647 | 270.95 | 0.92996 | 177.85 | 5.2375 | 334.26 | 1.1794 | 258.51 | 3.1107 | 399.39 | 1.2931 | 287.99 | 6.4485 | 414.86 | 2.4659
51.901 | 2.664 | 225.96 | 0.15128 | 76.428 | 1.8073 | 210.68 | 0.26567 | 219.63 | 0.35304 | 412.79 | 0.15387 | 132.15 | 1.2685 | 367.94 | 0.22338 | 126.97 | 2.9004 | 242.97 | 0.77677 | 131.62 | 4.7628 | 285.7 | 0.83422 | 181.8 | 4.7915 | 354.23 | 1.0387 | 269.06 | 2.7534 | 419.44 | 1.1607 | 292.93 | 5.8935 | 429.63 | 2.2328
54.02 | 2.3723 | 247.24 | 0.13099 | 80.668 | 1.5634 | 235.65 | 0.21827 | 238.16 | 0.30054 | 449.41 | 0.13464 | 139.9 | 1.1172 | 397.39 | 0.19549 | 131.62 | 2.5905 | 252.88 | 0.71549 | 134.15 | 4.4231 | 300.35 | 0.75271 | 186.41 | 4.3704 | 379.91 | 0.89384 | 277.25 | 2.4989 | 445.83 | 1.005 | 299.44 | 5.306 | 441.83 | 2.0699
56.903 | 2.0377 | 269.98 | 0.11462 | 84.974 | 1.37 | 266.23 | 0.17706 | 260.32 | 0.25179 | 491.73 | 0.1171 | 149 | 0.9732 | 430.49 | 0.17083 | 136.72 | 2.3299 | 267.45 | 0.63939 | 136.86 | 4.0953 | 312.6 | 0.69407 | 190.55 | 4.0182 | 400.59 | 0.79772 | 289.44 | 2.2141 | 473.87 | 0.88259 | 305.8 | 4.83 | 458.49 | 1.8745
59.582 | 1.7929 | 295.11 | 0.10039 | 88.885 | 1.22 | 300.77 | 0.14514 | 282.57 | 0.21477 | 551.11 | 0.099273 | 157.74 | 0.86316 | 466.35 | 0.14998 | 141.16 | 2.1337 | 277.81 | 0.59182 | 140.74 | 3.7503 | 328.63 | 0.62955 | 196.75 | 3.6105 | 427.92 | 0.69439 | 300.64 | 1.9914 | 501.66 | 0.78308 | 312.29 | 4.4099 | 482.48 | 1.6323
62.636 | 1.5634 | 321.93 | 0.08913 | 94.57 | 1.0511 | 341.84 | 0.11863 | 303.36 | 0.1869 | 596.41 | 0.089079 | 171.56 | 0.72169 | 498.17 | 0.13502 | 145.9 | 1.9422 | 291.47 | 0.53803 | 145.61 | 3.3563 | 347.21 | 0.56549 | 204.16 | 3.2441 | 445.38 | 0.63768 | 311.04 | 1.82 | 534.29 | 0.68751 | 318.28 | 4.0749 | 510.78 | 1.415
65.258 | 1.4005 | 357.22 | 0.078432 | 100.72 | 0.9056 | 385.04 | 0.099794 | 322.44 | 0.16511 | 644.15 | 0.080955 | 192.28 | 0.57398 | 545.63 | 0.11729 | 150.19 | 1.8073 | 306.72 | 0.48798 | 151.1 | 2.9798 | 372.39 | 0.49327 | 210.59 | 2.9442 | 463.1 | 0.59033 | 322.44 | 1.66 | 560.56 | 0.62364 | 326.99 | 3.6908 | 543.45 | 1.2191
68.879 | 1.2273 | 390.08 | 0.072069 | 107.06 | 0.78887 | 422.14 | 0.087809 | 355.29 | 0.13654 | 709.05 | 0.073625 | 210.17 | 0.4828 | 583.43 | 0.10635 | 155.39 | 1.6567 | 329.95 | 0.42411 | 157.74 | 2.6375 | 415.69 | 0.40187 | 218.1 | 2.6614 | 482.96 | 0.54303 | 333.93 | 1.5141 | 591.07 | 0.56231 | 335.27 | 3.3731 | 569.6 | 1.0921
71.833 | 1.1072 | 435 | 0.065565 | 113.11 | 0.69617 | 471.7 | 0.077267 | 382.96 | 0.11764 | 768.88 | 0.068417 | 230.66 | 0.40165 | 624.49 | 0.096489 | 160.28 | 1.5263 | 354.58 | 0.36971 | 165.16 | 2.316 | 458.49 | 0.33538 | 224.51 | 2.4421 | 510.78 | 0.48886 | 347.56 | 1.3687 | 623.86 | 0.50596 | 345.48 | 3.0644 | 609.07 | 0.93479
74.84 | 1.0049 | 475.49 | 0.061233 | 121.55 | 0.59502 | 521.83 | 0.070174 | 412.79 | 0.10115 | 829.59 | 0.06432 | 249.37 | 0.34295 | 685.35 | 0.085054 | 166.49 | 1.3935 | 402.19 | 0.29358 | 172.59 | 2.05 | 525.28 | 0.26225 | 231.58 | 2.2185 | 542.9 | 0.43332 | 359.22 | 1.266 | 661.78 | 0.45223 | 358.14 | 2.7562 | 638.38 | 0.8415
79.547 | 0.87183 | 535.04 | 0.056542 | 129.59 | 0.52092 | 569.83 | 0.065091 | 449.41 | 0.085849 | 897.79 | 0.060641 | 275.6 | 0.28079 | 755.16 | 0.076472 | 173.11 | 1.2622 | 441.39 | 0.24871 | 178.92 | 1.8605 | 606.64 | 0.20388 | 239.35 | 2.0256 | 583.43 | 0.38027 | 370.9 | 1.1792 | 723.38 | 0.38708 | 370.16 | 2.4964 | 673.13 | 0.75092
84.044 | 0.77093 | 577.87 | 0.054023 | 137.6 | 0.45787 | 642.49 | 0.059565 | 491.73 | 0.071492 | 980.37 | 0.057276 | 294.4 | 0.24557 | 822.98 | 0.070519 | 180.54 | 1.1478 | 485.38 | 0.21083 | 186.03 | 1.6851 | 659.8 | 0.17704 | 246.15 | 1.8754 | 618.89 | 0.34254 | 385.65 | 1.0713 | 805.88 | 0.31858 | 382.96 | 2.2633 | 713.32 | 0.66186
90.138 | 0.65563 | 626.62 | 0.05184 | 145.96 | 0.40448 | 703.69 | 0.05616 | 551.11 | 0.056974 | 1053.6 | 0.054841 | 319.24 | 0.20926 | 898.68 | 0.065432 | 189.41 | 1.0293 | 530.56 | 0.18133 | 193.43 | 1.5293 | 716.9 | 0.15445 | 256.71 | 1.6885 | 663.1 | 0.30223 | 399.39 | 0.98594 | 888.85 | 0.26771 | 399.79 | 2.0074 | 756.67 | 0.58509
98.627 | 0.5384 | 672.73 | 0.050107 | 157.01 | 0.34709 | 807.82 | 0.052034 | 596.41 | 0.048744 | 1151.6 | 0.052271 | 340.68 | 0.18339 | 962.88 | 0.062048 | 201.33 | 0.89748 | 584.02 | 0.15493 | 203.35 | 1.3578 | 764.28 | 0.1395 | 269.6 | 1.4856 | 719.77 | 0.26058 | 419.44 | 0.88501 | 998.18 | 0.21888 | 414.86 | 1.8164 | 801.06 | 0.52002
107.27 | 0.44971 | 708.64 | 0.049 | 166.39 | 0.30846 | 873.36 | 0.050152 | 644.15 | 0.041955 | 1222.8 | 0.050747 | 367.94 | 0.15721 | 1042 | 0.05868 | 213.35 | 0.78808 | 648.03 | 0.13134 | 211.65 | 1.2286 | 820.51 | 0.12481 | 282.01 | 1.3376 | 789.13 | 0.22185 | 445.83 | 0.77479 | 1102.1 | 0.18516 | 429.63 | 1.6468 | 866.04 | 0.44316
120.34 | 0.35199 | 709 | 0.045 | 178.1 | 0.26816 | 921.81 | 0.049 | 709.05 | 0.034625 | 1295.9 | 0.04945 | 397.39 | 0.13504 | 1120.9 | 0.056023 | 224.51 | 0.70669 | 708.35 | 0.11477 | 222.5 | 1.0973 | 901.38 | 0.10856 | 297.65 | 1.178 | 866.04 | 0.18898 | 473.87 | 0.67898 | 1196.2 | 0.162 | 441.83 | 1.5278 | 914.09 | 0.39803
132.2 | 0.29021 | 1000 | 0.045 | 191.97 | 0.23012 | 922 | 0.045 | 768.88 | 0.029417 | 1326 | 0.049 | 430.49 | 0.11496 | 1197.4 | 0.053933 | 234.38 | 0.64522 | 778.94 | 0.099983 | 233.44 | 0.9889 | 954.26 | 0.10018 | 316.06 | 1.0293 | 994.19 | 0.15033 | 501.66 | 0.6016 | 1295.9 | 0.14261 | 458.49 | 1.3949 | 968.68 | 0.35611
143.07 | 0.24705 | 1417.28 | 0.045 | 210.68 | 0.19183 | 1500 | 0.045 | 829.59 | 0.02532 | 1327 | 0.045 | 466.35 | 0.097865 | 1277.8 | 0.0521 | 242.97 | 0.5974 | 848.04 | 0.089013 | 244.43 | 0.89569 | 1016.3 | 0.0918 | 334.26 | 0.90923 | 1087.8 | 0.13033 | 534.29 | 0.52826 | 1423.6 | 0.12372 | 482.48 | 1.2298 | 1026.5 | 0.31731
155.76 | 0.20864 | 1418 | 0.043 | 235.65 | 0.15302 | 1843.62 | 0.045 | 897.79 | 0.021641 | 2000 | 0.045 | 498.17 | 0.085935 | 1343.4 | 0.050829 | 252.88 | 0.54872 | 926.98 | 0.079796 | 258.25 | 0.796 | 1073.8 | 0.085305 | 354.23 | 0.79919 | 1190.3 | 0.11394 | 560.56 | 0.47847 | 1519.2 | 0.11229 | 510.78 | 1.0723 | 1090 | 0.28303
171.46 | 0.17236 | 12500 | 0.043 | 266.23 | 0.12013 | 1844 | 0.043 | 980.37 | 0.018276 | 2652 | 0.045 | 545.63 | 0.071564 | 1396.8 | 0.049964 | 267.45 | 0.49009 | 1010.2 | 0.073384 | 270.95 | 0.71953 | 1127.7 | 0.080165 | 379.91 | 0.68512 | 1298.5 | 0.10013 | 591.07 | 0.42949 | 1632.6 | 0.10121 | 543.45 | 0.92389 | 1183.1 | 0.24301
190.44 | 0.13943 | 25000 | 0.043 | 300.77 | 0.093746 | 12500 | 0.043 | 1053.6 | 0.015841 | 2653 | 0.043 | 583.43 | 0.062652 | 1436.5 | 0.049377 | 277.81 | 0.45196 | 1090 | 0.068506 | 285.7 | 0.64522 | 1202.2 | 0.075255 | 400.59 | 0.60947 | 1417.9 | 0.088747 | 623.86 | 0.38939 | 1786.3 | 0.089465 | 569.6 | 0.82848 | 1295.9 | 0.2071
207.13 | 0.11799 |  |  | 341.84 | 0.072718 | 25000 | 0.043 | 1151.6 | 0.013271 | 12500 | 0.043 | 624.49 | 0.054794 | 1462.5 | 0.049 | 291.47 | 0.41018 | 1185.5 | 0.063968 | 300.35 | 0.58091 | 1265.1 | 0.071805 | 427.92 | 0.53091 | 1573.3 | 0.078197 | 661.78 | 0.34571 | 1942.9 | 0.080454 | 609.07 | 0.71166 | 1435 | 0.17381
225.96 | 0.099047 |  |  | 385.04 | 0.057546 |  |  | 1222.8 | 0.011747 | 25000 | 0.043 | 685.35 | 0.045403 | 1463 | 0.045 | 306.72 | 0.36893 | 1298.4 | 0.059792 | 312.6 | 0.53357 | 1328.7 | 0.068654 | 445.38 | 0.49058 | 1752.7 | 0.070677 | 723.38 | 0.29108 | 2083.8 | 0.075219 | 638.38 | 0.64072 | 1563.9 | 0.15086
247.24 | 0.082318 |  |  | 422.14 | 0.047588 |  |  | 1295.9 | 0.01045 |  |  | 755.16 | 0.037472 | 2000 | 0.045 | 329.95 | 0.31977 | 1453.8 | 0.055686 | 328.63 | 0.4828 | 1394 | 0.065939 | 463.1 | 0.45106 | 1915.9 | 0.065485 | 805.88 | 0.23571 | 2221.5 | 0.070868 | 673.13 | 0.57055 | 1709.5 | 0.13097
269.98 | 0.06931 |  |  | 471.7 | 0.038267 |  |  | 1326 | 0.01 |  |  | 822.98 | 0.031519 | 2925 | 0.045 | 354.58 | 0.27578 | 1559.2 | 0.053463 | 347.21 | 0.43424 | 1496.6 | 0.062443 | 482.96 | 0.41347 | 2125.8 | 0.060641 | 888.85 | 0.19395 | 2365.9 | 0.067039 | 713.32 | 0.5025 | 1861.1 | 0.11513
295.11 | 0.057893 |  |  | 521.83 | 0.031174 | [6 empty] | 898.68 | 0.026432 | 2926 | 0.043 | 402.19 | 0.21413 | 1649 | 0.051956 | 372.39 | 0.37638 | 1576.4 | 0.060064 | 510.78 | 0.37077 | 2296 | 0.057571 | 998.18 | 0.15394 | 2542.6 | 0.063376 | 756.67 | 0.4408 | 2067.2 | 0.098996
321.93 | 0.048647 |  |  | 569.83 | 0.026091 | [6 empty] | 962.88 | 0.023048 | 12500 | 0.043 | 441.39 | 0.17797 | 1724.9 | 0.050829 | 415.69 | 0.30145 | 1685.7 | 0.057441 | 542.9 | 0.33016 | 2464.9 | 0.055112 | 1102.1 | 0.1268 | 2787.6 | 0.059299 | 801.06 | 0.39057 | 2246.1 | 0.088283
357.22 | 0.039432 |  |  | 642.49 | 0.020565 | [6 empty] | 1042 | 0.01968 | 25000 | 0.043 | 485.38 | 0.14761 | 1798.9 | 0.04992 | 458.49 | 0.24804 | 1781 | 0.05557 | 583.43 | 0.28589 | 2659.6 | 0.052868 | 1196.2 | 0.10848 | 3025.8 | 0.056194 | 866.04 | 0.33182 | 2509.7 | 0.07769
390.08 | 0.033069 |  |  | 703.69 | 0.01716 | [6 empty] | 1120.9 | 0.017023 |  |  | 530.56 | 0.12367 | 1850 | 0.049325 | 525.28 | 0.18878 | 1893 | 0.053652 | 618.89 | 0.25356 | 2762.6 | 0.051827 | 1295.9 | 0.092628 | 3258.2 | 0.053903 | 914.09 | 0.29489 | 2743.3 | 0.071414
435 | 0.026565 |  |  | 807.82 | 0.013034 | [6 empty] | 1197.4 | 0.014933 |  |  | 584.02 | 0.10206 | 1877.9 | 0.049 | 606.64 | 0.14197 | 1984.1 | 0.052378 | 663.1 | 0.22132 | 2875.3 | 0.050889 | 1423.6 | 0.076906 | 3543.7 | 0.051599 | 968.68 | 0.26076 | 3034.9 | 0.065406
475.49 | 0.022233 |  |  | 873.36 | 0.011152 | [6 empty] | 1277.8 | 0.0131 |  |  | 648.03 | 0.082896 | 1878 | 0.045 | 659.8 | 0.12013 | 2061 | 0.051386 | 719.77 | 0.18784 | 2980.7 | 0.050041 | 1519.2 | 0.067599 | 3800.6 | 0.049942 | 1026.5 | 0.23058 | 3261.4 | 0.06191
535.04 | 0.017542 |  |  | 921.81 | 0.01 | [6 empty] | 1343.4 | 0.011829 |  |  | 708.35 | 0.069588 | 2500 | 0.045 | 716.9 | 0.10155 | 2138.7 | 0.050514 | 789.13 | 0.15612 | 3090 | 0.049336 | 1632.6 | 0.058533 | 3916.4 | 0.049325 | 1090 | 0.2043 | 3536.6 | 0.058503
577.87 | 0.015023 | [10 empty] | 1396.8 | 0.010964 |  |  | 778.94 | 0.057661 | 3755.8 | 0.045 | 764.28 | 0.089442 | 2208.2 | 0.049811 | 866.04 | 0.12936 | 3133.6 | 0.049 | 1786.3 | 0.049136 | 3967.7 | 0.049 | 1183.1 | 0.17271 | 3789.3 | 0.056023
626.62 | 0.01284 | [10 empty] | 1436.5 | 0.010377 |  |  | 848.04 | 0.048696 | 3756 | 0.043 | 820.51 | 0.077913 | 2261.8 | 0.049284 | 994.19 | 0.098651 | 3134 | 0.045 | 1942.9 | 0.041454 | 3968 | 0.045 | 1295.9 | 0.14382 | 4142 | 0.053248
672.73 | 0.011107 | [10 empty] | 1462.5 | 0.01 |  |  | 926.98 | 0.040796 | 12500 | 0.043 | 901.38 | 0.064689 | 2289.1 | 0.049 | 1087.8 | 0.082154 | 4500 | 0.045 | 2083.8 | 0.036219 | 6000 | 0.045 | 1435 | 0.11717 | 4354.3 | 0.051879
708.64 | 0.01 | [14 empty] | 1010.2 | 0.034384 | 25000 | 0.043 | 954.26 | 0.057777 | 2290 | 0.045 | 1190.3 | 0.068758 | 6267.2 | 0.045 | 2221.5 | 0.031868 | 7935.4 | 0.045 | 1563.9 | 0.098651 | 4573 | 0.050688
[16 empty] | 1090 | 0.029506 |  |  | 1016.3 | 0.050734 | 3500 | 0.045 | 1298.5 | 0.057546 | 6268 | 0.043 | 2365.9 | 0.028039 | 7936 | 0.043 | 1709.5 | 0.082648 | 4731.2 | 0.049931
[16 empty] | 1185.5 | 0.024968 |  |  | 1073.8 | 0.045403 | 4578.2 | 0.045 | 1417.9 | 0.048308 | 12500 | 0.043 | 2542.6 | 0.024376 | 12500 | 0.043 | 1861.1 | 0.069937 | 4855.8 | 0.049377
[16 empty] | 1298.4 | 0.020792 |  |  | 1127.7 | 0.041165 | 4579 | 0.043 | 1573.3 | 0.039197 | 25000 | 0.043 | 2787.6 | 0.020299 | 25000 | 0.043 | 2067.2 | 0.056917 | 4929.2 | 0.049
[16 empty] | 1453.8 | 0.016686 |  |  | 1202.2 | 0.036255 | 12500 | 0.043 | 1752.7 | 0.031677 |  |  | 3025.8 | 0.017194 |  |  | 2246.1 | 0.048019 | 4930 | 0.045
[16 empty] | 1559.2 | 0.014463 |  |  | 1265.1 | 0.032805 | 25000 | 0.043 | 1915.9 | 0.026485 |  |  | 3258.2 | 0.014903 |  |  | 2509.7 | 0.03869 | 7500 | 0.045
[16 empty] | 1649 | 0.012956 |  |  | 1328.7 | 0.029654 |  |  | 2125.8 | 0.021641 |  |  | 3543.7 | 0.012599 |  |  | 2743.3 | 0.032414 | 9858.4 | 0.045
[16 empty] | 1724.9 | 0.011829 |  |  | 1394 | 0.026939 |  |  | 2296 | 0.018571 |  |  | 3800.6 | 0.010942 |  |  | 3034.9 | 0.026406 | 9859 | 0.043
[16 empty] | 1798.9 | 0.01092 |  |  | 1496.6 | 0.023443 |  |  | 2464.9 | 0.016112 |  |  | 3916.4 | 0.010325 |  |  | 3261.4 | 0.02291 | 12500 | 0.043
[16 empty] | 1850 | 0.010325 |  |  | 1576.4 | 0.021064 |  |  | 2659.6 | 0.013868 |  |  | 3967.7 | 0.01 |  |  | 3536.6 | 0.019503 | 25000 | 0.043
[16 empty] | 1877.9 | 0.01 |  |  | 1685.7 | 0.018441 |  |  | 2762.6 | 0.012827 | [6 empty] | 3789.3 | 0.017023
[20 empty] | 1781 | 0.01657 |  |  | 2875.3 | 0.011889 | [6 empty] | 4142 | 0.014248
[20 empty] | 1893 | 0.014652 |  |  | 2980.7 | 0.011041 | [6 empty] | 4354.3 | 0.012879
[20 empty] | 1984.1 | 0.013378 |  |  | 3090 | 0.010336 | [6 empty] | 4573 | 0.011688
[20 empty] | 2061 | 0.012386 |  |  | 3133.6 | 0.01 | [6 empty] | 4731.2 | 0.010931
[20 empty] | 2138.7 | 0.011514 | [10 empty] | 4855.8 | 0.010377
[20 empty] | 2208.2 | 0.010811 | [10 empty] | 4929.2 | 0.01
[20 empty] | 2261.8 | 0.010284
[20 empty] | 2289.1 | 0.01

## 50 Hz, 660-1 CT Ratio
S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0
S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018
50 Hz, 660:1 CT Ratio | [11 empty] | 50 Hz, 660:1 CT Ratio | [11 empty] | 50 Hz, 660:1 CT Ratio | [11 empty] | 50 Hz, 660:1 CT Ratio | [11 empty] | 50 Hz, 660:1 CT Ratio | [11 empty] | 50 Hz, 660:1 CT Ratio
Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information.
8K |  |  |  | 10K |  |  |  | 12K |  |  |  | 15K |  |  |  | 20K |  |  |  | 25K |  |  |  | 30K |  |  |  | 40K |  |  |  | 50K |  |  |  | 65K |  |  |  | 80K |  |  |  | 100K |  |  |  | 125K |  |  |  | 150K |  |  |  | 175K |  |  |  | 200K
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
15.601 | 1000 | 18.904 | 1000 | 20.396 | 1000 | 23.721 | 1000 | 27.313 | 1000 | 30.488 | 1000 | 32.896 | 1000 | 36.942 | 1000 | 42.451 | 1000 | 47.911 | 1000 | 49.597 | 1000 | 55.42 | 1000 | 59.915 | 1000 | 67.893 | 1000 | 79.594 | 1000 | 89.205 | 1000 | 97.997 | 1000 | 109.06 | 1000 | 128.37 | 1000 | 143.3 | 1000 | 159.32 | 1000 | 178.03 | 1000 | 195.18 | 1000 | 217.44 | 1000 | 274.55 | 1000 | 312.55 | 1000 | 329.65 | 1000 | 378.1 | 1000 | 401.85 | 1000 | 448.4 | 1000 | 479.75 | 1000 | 570 | 1000
15.601 | 302.73 | 18.904 | 41.674 | 20.396 | 302.43 | 23.721 | 31.681 | 27.313 | 303.64 | 30.488 | 242.979 | 32.896 | 300.92 | 36.942 | 147.519 | 42.451 | 303.64 | 47.911 | 161.599 | 49.597 | 602.96 | 55.42 | 490.149 | 59.915 | 608.41 | 67.893 | 81.774 | 79.594 | 609.02 | 89.205 | 452.689 | 97.997 | 602.36 | 109.06 | 557.549 | 128.37 | 601.76 | 143.3 | 274.409 | 159.32 | 605.98 | 178.03 | 538.399 | 195.18 | 601.15 | 217.44 | 569.259 | 274.55 | 600 | 312.55 | 170.109 | 329.65 | 600 | 378.1 | 164.259 | 401.85 | 600 | 448.4 | 559.789 | 479.75 | 600 | 570 | 162.329
15.742 | 49.891 | 19.285 | 28.471 | 20.437 | 116.85 | 24.127 | 20.643 | 27.34 | 270.66 | 31.104 | 96.608 | 32.962 | 270.93 | 37.5 | 75.519 | 42.621 | 261.09 | 48.684 | 94.887 | 49.996 | 26.492 | 57.165 | 18.014 | 60.156 | 161.23 | 69.612 | 40.642 | 79.753 | 578.16 | 90.462 | 246.119 | 98.095 | 568.98 | 110.38 | 322.719 | 128.5 | 569.55 | 145.03 | 129.799 | 159.96 | 559.39 | 181.08 | 308.659 | 195.96 | 553.83 | 220.29 | 351.899 | 275.5 | 300 | 340.1 | 64.209 | 332.5 | 300 | 408.5 | 66.843 | 413.25 | 300 | 482.6 | 150.709 | 494 | 300 | 625.1 | 64.79
15.869 | 42.515 | 19.833 | 20.078 | 20.457 | 94.618 | 24.738 | 14.595 | 27.449 | 226.98 | 31.574 | 42.195 | 33.061 | 223.15 | 38.029 | 44.968 | 42.835 | 212.91 | 49.519 | 45.224 | 50.599 | 22.04 | 58.67 | 14.518 | 60.336 | 117.2 | 71.517 | 25.39 | 79.913 | 513.81 | 92.752 | 96.975 | 98.389 | 488.26 | 112.05 | 102.719 | 128.5 | 461.21 | 146.78 | 94.061 | 160.44 | 498.62 | 184.37 | 184.099 | 196.75 | 446.68 | 222.95 | 241.709 | 277.4 | 200 | 365.75 | 36.992 | 334.4 | 200 | 446.5 | 35.771 | 422.75 | 200 | 517.75 | 72.508 | 503.5 | 200 | 682.1 | 34.271
15.996 | 35.796 | 20.437 | 14.753 | 20.478 | 78.48 | 25.491 | 10.222 | 27.559 | 188.83 | 32.438 | 17.121 | 33.16 | 181.43 | 38.565 | 34.532 | 43.049 | 167.81 | 50.62 | 28.278 | 51.415 | 18.063 | 60.336 | 11.532 | 60.821 | 88.31 | 73.474 | 18.522 | 80.313 | 422.36 | 94.532 | 61.887 | 98.685 | 424.48 | 113.63 | 66.198 | 128.5 | 359.55 | 148.7 | 69.508 | 161.41 | 415.24 | 187.72 | 113.959 | 197.93 | 362.07 | 225.64 | 185.449 | 287.85 | 100 | 427.5 | 15.999 | 348.65 | 100 | 515.85 | 16.613 | 448.4 | 100 | 555.75 | 39.667 | 530.1 | 100 | 798 | 15.955
16.189 | 29.84 | 21.144 | 10.949 | 20.519 | 63.998 | 26.373 | 7.8567 | 27.67 | 150.78 | 33.36 | 12.074 | 33.226 | 149.58 | 39.109 | 26.976 | 43.222 | 135.08 | 51.643 | 20.017 | 52.349 | 15.224 | 62.298 | 9.75 | 61.248 | 67.684 | 75.787 | 13.748 | 80.716 | 336.25 | 96.249 | 41.64 | 99.081 | 347.88 | 115.11 | 46.687 | 128.89 | 278.62 | 150.8 | 50.542 | 162.54 | 325.99 | 191.7 | 79.514 | 198.93 | 299.12 | 228.82 | 141.939 | 312.55 | 50 | 513 | 7.4923 | 378.1 | 50 | 617.5 | 7.5333 | 482.6 | 50 | 647.9 | 16.126 | 570 | 50 | 950 | 7.6302
16.401 | 25.735 | 21.919 | 8.1881 | 20.498 | 52.24 | 27.231 | 6.2353 | 27.836 | 119.56 | 34.273 | 9.9614 | 33.36 | 119.68 | 39.899 | 19.988 | 43.526 | 107.97 | 52.844 | 15.62 | 53.353 | 13.129 | 64.582 | 8.3557 | 61.74 | 54.209 | 77.706 | 11.372 | 81.283 | 255.66 | 98.193 | 29.509 | 99.478 | 282.55 | 116.86 | 33.143 | 129.01 | 216.34 | 152.77 | 38.814 | 163.68 | 258.75 | 195.96 | 54.625 | 200.12 | 251.6 | 232.04 | 112.819 | 340.1 | 30 | 595.65 | 4.3303 | 408.5 | 30 | 717.25 | 4.3265 | 517.75 | 30 | 779 | 7.4607 | 625.1 | 30 | 1102 | 4.3403
16.632 | 21.799 | 22.836 | 6.4091 | 20.519 | 45.461 | 27.948 | 5.4731 | 27.948 | 100.17 | 35.281 | 8.1124 | 33.493 | 99.768 | 40.705 | 16.098 | 43.831 | 85.528 | 54.182 | 12.052 | 54.16 | 11.645 | 66.949 | 7.2326 | 62.298 | 43.417 | 80.153 | 9.2222 | 81.69 | 201.51 | 100.08 | 23.27 | 99.677 | 223.6 | 118.74 | 24.695 | 129.4 | 170.69 | 155.23 | 31.524 | 164.83 | 207.03 | 199.92 | 40.811 | 201.33 | 209.11 | 235.32 | 92.087 | 365.75 | 20 | 674.5 | 2.8491 | 446.5 | 20 | 807.5 | 2.8969 | 555.75 | 20 | 902.5 | 4.3537 | 682.1 | 20 | 1244.5 | 2.8708
16.917 | 18.557 | 23.626 | 5.3937 | 20.56 | 38.086 | 28.944 | 4.6726 | 28.088 | 79.986 | 36.319 | 6.7955 | 33.594 | 81.683 | 41.652 | 13.148 | 43.963 | 69.467 | 55.498 | 10.0012 | 55.42 | 10.205 | 69.403 | 6.2399 | 62.924 | 35.299 | 82.346 | 7.8024 | 82.182 | 155.07 | 102.4 | 18.068 | 99.976 | 173.79 | 120.53 | 20.444 | 129.92 | 141.01 | 158.21 | 24.942 | 166.16 | 159.31 | 203.76 | 30.821 | 203.35 | 178.19 | 238.63 | 76.116 | 427.5 | 10 | 855 | 1.3897 | 515.85 | 10 | 1026 | 1.3856 | 647.9 | 10 | 1035.5 | 2.7579 | 798 | 10 | 1577 | 1.3903
17.19 | 16.068 | 24.788 | 4.323 | 20.684 | 32.293 | 30.095 | 3.9818 | 28.201 | 64.062 | 37.313 | 5.8851 | 33.762 | 67.549 | 42.664 | 10.653 | 44.272 | 55.249 | 56.903 | 8.3825 | 57.165 | 8.8804 | 73.401 | 5.2035 | 63.493 | 30.412 | 84.769 | 6.6148 | 82.594 | 126.58 | 103.95 | 15.174 | 100.28 | 127.47 | 122.85 | 15.797 | 130.97 | 115.45 | 160.44 | 21.016 | 167.99 | 124.19 | 207.67 | 25.129 | 205.39 | 146.77 | 243.7 | 59.009 | 513 | 5 | 1092.5 | 0.70254 | 617.5 | 5 | 1320.5 | 0.69682 | 779 | 5 | 1301.5 | 1.4053 | 950 | 5 | 2042.5 | 0.69212
17.468 | 14.011 | 25.851 | 3.5958 | 20.746 | 28.271 | 31.26 | 3.4389 | 28.285 | 52.66 | 38.488 | 5.0577 | 33.932 | 55.693 | 43.875 | 8.6918 | 44.538 | 45.597 | 58.46 | 7.1152 | 58.67 | 7.9236 | 77.396 | 4.4028 | 64.067 | 26.466 | 87.438 | 5.7058 | 83.091 | 104.88 | 106.58 | 12.08 | 100.68 | 105.94 | 125.08 | 13.473 | 131.75 | 98.087 | 163.68 | 17.003 | 170.36 | 94.903 | 211.65 | 20.167 | 207.46 | 122.1 | 247.63 | 50.071 | 595.65 | 3 | 1349 | 0.41622 | 717.25 | 3 | 1615 | 0.42094 | 902.5 | 3 | 1681.5 | 0.69394 | 1102 | 3 | 2508 | 0.41891
17.803 | 12.096 | 27.014 | 3.0234 | 20.85 | 24.553 | 32.601 | 3.0184 | 28.37 | 43.243 | 39.344 | 4.5715 | 34.17 | 45.917 | 45.076 | 7.4262 | 44.941 | 37.146 | 60.18 | 6.0812 | 60.336 | 7.0628 | 81.69 | 3.7816 | 64.906 | 22.507 | 90.734 | 4.9085 | 83.675 | 85.871 | 108.85 | 10.167 | 101.18 | 86.995 | 127.22 | 11.449 | 132.94 | 76.39 | 166.82 | 14.504 | 172.59 | 75.554 | 215.71 | 16.501 | 209.96 | 101.58 | 251.62 | 41.395 | 674.5 | 2 | 1615 | 0.28258 | 807.5 | 2 | 1947.5 | 0.28027 | 1035.5 | 2 | 2061.5 | 0.4197 | 1244.5 | 2 | 2973.5 | 0.28604
18.162 | 10.473 | 28.314 | 2.5415 | 21.102 | 20.839 | 33.796 | 2.7108 | 28.484 | 35.868 | 40.786 | 3.8823 | 34.376 | 38.584 | 46.263 | 6.4524 | 45.347 | 29.721 | 62.075 | 5.1133 | 62.298 | 6.2641 | 84.854 | 3.4244 | 65.492 | 19.942 | 94.248 | 4.1819 | 84.6 | 67.145 | 111.27 | 8.5035 | 101.49 | 74.877 | 129.4 | 10.077 | 134.01 | 64.062 | 170.36 | 12.279 | 175.2 | 59.196 | 221.17 | 13.576 | 212.29 | 88.752 | 255.94 | 34.89 | 855 | 1 | 2194.5 | 0.15589 | 1026 | 1 | 2669.5 | 0.15506 | 1301.5 | 1 | 2479.5 | 0.28107 | 1577 | 1 | 4085 | 0.15485
18.529 | 9.1967 | 29.676 | 2.1685 | 21.292 | 18.026 | 35.564 | 2.3516 | 28.627 | 29.9 | 42.028 | 3.4193 | 34.756 | 32.683 | 47.959 | 5.3534 | 45.849 | 23.923 | 64.351 | 4.3759 | 64.582 | 5.5392 | 90.011 | 2.9333 | 66.349 | 17.705 | 98.291 | 3.6304 | 85.365 | 52.712 | 113.86 | 7.2896 | 102.3 | 61.121 | 131.62 | 8.9125 | 135.09 | 53.455 | 173.8 | 10.715 | 178.03 | 45.872 | 225.86 | 11.434 | 214.63 | 76.619 | 260.85 | 29 | 1092.5 | 0.5 | 3040 | 0.094 | 1320.5 | 0.5 | 3676.5 | 0.094 | 1681.5 | 0.5 | 3391.5 | 0.15526 | 2042.5 | 0.5 | 5633.5 | 0.094
18.904 | 8.1894 | 31.323 | 1.8432 | 21.549 | 15.531 | 37.053 | 2.1004 | 28.742 | 25.709 | 43.308 | 3.0627 | 35 | 28.555 | 49.767 | 4.5674 | 46.449 | 20.102 | 66.709 | 3.8261 | 66.949 | 4.9424 | 95.196 | 2.5428 | 67.893 | 14.152 | 102.82 | 3.1778 | 86.395 | 42.985 | 117.09 | 6.1416 | 102.81 | 51.876 | 134.15 | 7.6762 | 136.86 | 40.766 | 177.85 | 9.3575 | 181.08 | 34.843 | 229.97 | 9.9804 | 217.44 | 64.447 | 265.85 | 23.686 | 1349 | 0.3 | 3895 | 0.074 | 1615 | 0.3 | 4655 | 0.074 | 2061.5 | 0.3 | 4702.5 | 0.094 | 2508 | 0.3 | 7172.5 | 0.074
19.285 | 7.2199 | 32.962 | 1.5898 | 21.788 | 13.611 | 38.642 | 1.8761 | 28.857 | 21.93 | 45.211 | 2.6468 | 35.387 | 23.923 | 51.901 | 3.7955 | 47.151 | 16.691 | 69.71 | 3.2546 | 69.403 | 4.4187 | 99.976 | 2.2706 | 69.612 | 11.668 | 107.98 | 2.7653 | 87.089 | 36.739 | 122.11 | 4.9277 | 103.64 | 42.728 | 136.86 | 6.8372 | 138.51 | 34.29 | 181.8 | 8.1299 | 184.37 | 28.47 | 234.38 | 8.6768 | 220.29 | 56.252 | 270.95 | 19.936 | 1615 | 0.2 | 4655 | 0.064 | 1947.5 | 0.2 | 5605 | 0.064 | 2479.5 | 0.2 | 5937.5 | 0.074 | 2973.5 | 0.2 | 8645 | 0.064
19.833 | 6.3843 | 34.652 | 1.3831 | 22.117 | 11.797 | 40.219 | 1.698 | 28.973 | 19.295 | 47.198 | 2.281 | 35.85 | 20.244 | 54.02 | 3.3179 | 47.911 | 14.095 | 72.919 | 2.8399 | 73.401 | 3.7691 | 106.26 | 1.9623 | 71.517 | 9.6296 | 113.17 | 2.4305 | 88.229 | 29.99 | 126.97 | 4.1405 | 104.47 | 35.796 | 140.74 | 5.8794 | 140.18 | 29.161 | 186.41 | 7.0139 | 187.72 | 22.756 | 240.07 | 7.3528 | 222.95 | 48.417 | 277.25 | 16.479 | 2194.5 | 0.1 | 6460 | 0.054 | 2669.5 | 0.1 | 7695 | 0.054 | 3391.5 | 0.1 | 7125 | 0.064 | 4085 | 0.1 | 11970 | 0.054
20.437 | 5.5614 | 36.611 | 1.1956 | 22.429 | 10.359 | 41.903 | 1.5319 | 29.118 | 17.476 | 49.419 | 1.993 | 36.392 | 16.909 | 56.903 | 2.8002 | 48.684 | 12.156 | 76.428 | 2.4776 | 77.396 | 3.2539 | 111.94 | 1.7494 | 73.474 | 8.1079 | 118.86 | 2.1502 | 89.205 | 25.479 | 131.62 | 3.6373 | 105.63 | 29.573 | 145.61 | 4.9607 | 141.73 | 25.942 | 190.55 | 6.2698 | 191.7 | 18.135 | 244.19 | 6.7221 | 225.64 | 42.813 | 282.85 | 14.192 | 3040 | 0.05 | 6461 | 0.049 | 3676.5 | 0.05 | 7696 | 0.049 | 4702.5 | 0.05 | 9880 | 0.054 | 5633.5 | 0.05 | 11971 | 0.049
21.144 | 4.7915 | 38.797 | 1.021 | 22.768 | 9.2243 | 43.352 | 1.4117 | 29.41 | 15.269 | 51.953 | 1.7363 | 36.942 | 14.51 | 59.582 | 2.4548 | 49.519 | 10.515 | 80.668 | 2.1306 | 81.69 | 2.8316 | 119.45 | 1.5102 | 75.787 | 6.7791 | 124.58 | 1.9103 | 90.462 | 21.176 | 136.72 | 3.2281 | 106.58 | 25.326 | 151.1 | 4.2563 | 143.3 | 22.328 | 196.75 | 5.4576 | 195.96 | 15.133 | 252.38 | 5.5737 | 228.82 | 37.034 | 287.99 | 12.381 | 3895 | 0.03 | 9000 | 0.049 | 4655 | 0.03 | 12500 | 0.049 | 5937.5 | 0.03 | 9881 | 0.049 | 7172.5 | 0.03 | 17500 | 0.049
21.919 | 4.1572 | 41.527 | 0.86807 | 23.112 | 8.2717 | 45.438 | 1.2579 | 29.647 | 13.761 | 54.399 | 1.531 | 37.5 | 12.589 | 62.636 | 2.1327 | 50.62 | 8.916 | 84.974 | 1.8333 | 84.854 | 2.5724 | 128.12 | 1.3035 | 77.706 | 5.9706 | 132.15 | 1.6489 | 92.752 | 16.23 | 141.16 | 2.924 | 107.66 | 21.908 | 157.74 | 3.6806 | 145.03 | 19.665 | 204.16 | 4.6521 | 199.92 | 12.729 | 258.51 | 4.8869 | 232.04 | 32.068 | 292.93 | 10.889 | 4655 | 0.02 | 12920 | 0.049 | 5605 | 0.02 | 15390 | 0.049 | 7125 | 0.02 | 15000 | 0.049 | 8645 | 0.02 | 23940 | 0.049
22.836 | 3.5746 | 44.095 | 0.75439 | 23.391 | 7.6205 | 47.815 | 1.1182 | 30.005 | 12.096 | 56.96 | 1.353 | 38.029 | 11.267 | 65.258 | 1.8977 | 51.643 | 7.79 | 88.885 | 1.6339 | 90.011 | 2.2341 | 137.13 | 1.1333 | 80.153 | 5.2218 | 139.9 | 1.449 | 94.532 | 13.368 | 145.9 | 2.6611 | 109.06 | 18.706 | 165.16 | 3.1874 | 146.78 | 17.424 | 210.59 | 4.1701 | 203.76 | 10.988 | 269.06 | 4.0808 | 235.32 | 27.711 | 299.44 | 9.4549 | 6460 | 0.01 | 12921 | 0.043 | 7695 | 0.01 | 15391 | 0.043 | 9880 | 0.01 | 19760 | 0.049 | 11970 | 0.01 | 23941 | 0.043
23.626 | 3.1545 | 47.529 | 0.63897 | 23.721 | 6.916 | 50.671 | 0.97706 | 30.488 | 10.653 | 59.88 | 1.1914 | 38.565 | 10.164 | 68.879 | 1.6454 | 52.844 | 6.7927 | 94.57 | 1.3935 | 95.196 | 1.9539 | 146.93 | 0.98973 | 82.346 | 4.6499 | 149 | 1.2571 | 96.249 | 11.38 | 150.19 | 2.4379 | 110.38 | 15.972 | 172.59 | 2.7859 | 148.7 | 15.438 | 218.1 | 3.6997 | 207.67 | 9.4863 | 277.25 | 3.5902 | 238.63 | 24.163 | 305.8 | 8.3741 |  |  | 20000 | 0.043 |  |  | 20000 | 0.043 |  |  | 19761 | 0.043 |  |  | 25000 | 0.043
24.788 | 2.6801 | 50.823 | 0.55213 | 24.127 | 6.3145 | 53.75 | 0.85875 | 31.104 | 9.2613 | 63.329 | 1.0374 | 39.109 | 9.1234 | 71.833 | 1.4726 | 54.182 | 5.9289 | 100.72 | 1.1932 | 99.976 | 1.7504 | 159.64 | 0.8391 | 84.769 | 4.1614 | 157.74 | 1.1116 | 98.193 | 9.8143 | 155.39 | 2.2225 | 112.05 | 13.913 | 178.92 | 2.5199 | 150.8 | 13.969 | 224.51 | 3.3655 | 211.65 | 8.3549 | 289.44 | 3.069 | 243.7 | 20.002 | 312.29 | 7.3855 |  |  | 25000 | 0.043 |  |  | 25000 | 0.043 |  |  | 22500 | 0.043
25.851 | 2.351 | 55.332 | 0.46299 | 24.738 | 5.6285 | 57.705 | 0.73807 | 31.574 | 8.3298 | 67.38 | 0.89984 | 39.899 | 8.0433 | 74.84 | 1.3261 | 55.498 | 5.2218 | 107.06 | 1.0357 | 106.26 | 1.5187 | 174.85 | 0.7064 | 87.438 | 3.7279 | 171.56 | 0.93136 | 100.08 | 8.5066 | 160.28 | 2.0443 | 113.63 | 12.023 | 186.03 | 2.2621 | 152.77 | 12.526 | 231.58 | 3.0773 | 215.71 | 7.3879 | 300.64 | 2.7375 | 247.63 | 17.354 | 318.28 | 6.7235 | [10 empty] | 25000 | 0.043
27.014 | 2.0541 | 59.761 | 0.39646 | 25.491 | 4.9523 | 63.076 | 0.61488 | 32.438 | 7.0276 | 71.332 | 0.79409 | 40.705 | 7.1552 | 79.547 | 1.1487 | 56.903 | 4.6313 | 113.11 | 0.91302 | 111.94 | 1.3551 | 193.24 | 0.58568 | 90.734 | 3.3262 | 192.28 | 0.73827 | 102.4 | 7.2852 | 166.49 | 1.8454 | 115.11 | 10.814 | 193.43 | 2.034 | 155.23 | 11.166 | 239.35 | 2.7848 | 221.17 | 6.4292 | 311.04 | 2.4623 | 251.62 | 15.285 | 326.99 | 5.8072
28.314 | 1.7804 | 64.932 | 0.33662 | 26.373 | 4.3269 | 69.501 | 0.50443 | 33.36 | 6.0427 | 74.989 | 0.70961 | 41.652 | 6.3525 | 84.044 | 1.0097 | 58.46 | 4.1489 | 121.55 | 0.78086 | 119.45 | 1.1816 | 219.63 | 0.462 | 94.248 | 2.9708 | 210.17 | 0.62381 | 103.95 | 6.5133 | 173.11 | 1.6747 | 116.86 | 9.6296 | 203.35 | 1.7887 | 158.21 | 9.9428 | 246.15 | 2.5726 | 225.86 | 5.6908 | 322.44 | 2.2275 | 255.94 | 13.354 | 335.27 | 5.175
29.676 | 1.554 | 71.261 | 0.28182 | 27.231 | 3.8723 | 74.392 | 0.44106 | 34.273 | 5.269 | 79.946 | 0.62177 | 42.664 | 5.5892 | 90.138 | 0.86265 | 60.18 | 3.6945 | 129.59 | 0.68114 | 128.12 | 1.0252 | 238.16 | 0.39836 | 98.291 | 2.6349 | 230.66 | 0.52287 | 106.58 | 5.7136 | 180.54 | 1.5062 | 118.74 | 8.5749 | 211.65 | 1.6193 | 160.44 | 8.9338 | 256.71 | 2.2859 | 229.97 | 5.1031 | 333.93 | 2.0323 | 260.85 | 11.552 | 345.48 | 4.5683
31.323 | 1.3349 | 78.598 | 0.23582 | 27.948 | 3.4793 | 79.15 | 0.39035 | 35.281 | 4.6128 | 87.212 | 0.51982 | 43.875 | 4.9177 | 98.627 | 0.71098 | 62.075 | 3.3296 | 137.6 | 0.60104 | 137.13 | 0.88767 | 260.32 | 0.33947 | 102.82 | 2.3463 | 249.37 | 0.4524 | 108.85 | 5.0827 | 189.41 | 1.3473 | 120.53 | 7.7125 | 222.5 | 1.4377 | 163.68 | 7.9633 | 269.6 | 1.9838 | 234.38 | 4.636 | 347.56 | 1.8228 | 265.85 | 10.154 | 358.14 | 3.9367
32.962 | 1.1593 | 87.825 | 0.19372 | 28.944 | 3.1107 | 84.213 | 0.3467 | 36.319 | 4.0142 | 94.855 | 0.44078 | 45.076 | 4.3529 | 107.27 | 0.59403 | 64.351 | 2.9768 | 145.96 | 0.53504 | 146.93 | 0.77402 | 282.57 | 0.29318 | 107.98 | 2.0623 | 275.6 | 0.37606 | 111.27 | 4.5533 | 201.33 | 1.1674 | 122.85 | 6.8953 | 233.44 | 1.2887 | 166.82 | 7.1624 | 282.01 | 1.7669 | 240.07 | 4.1822 | 359.22 | 1.6781 | 270.95 | 9.0507 | 370.16 | 3.5091
34.652 | 1.0109 | 96.965 | 0.16394 | 30.095 | 2.7645 | 89.958 | 0.30551 | 37.313 | 3.5603 | 101.83 | 0.38481 | 46.263 | 3.8878 | 120.34 | 0.46957 | 66.709 | 2.6747 | 157.01 | 0.46198 | 159.64 | 0.65892 | 303.36 | 0.25848 | 113.17 | 1.8255 | 294.4 | 0.33256 | 113.86 | 4.1614 | 213.35 | 1.0272 | 125.08 | 6.1709 | 244.43 | 1.1577 | 170.36 | 6.4163 | 297.65 | 1.5511 | 244.19 | 3.8299 | 370.9 | 1.5543 | 277.25 | 7.8605 | 382.96 | 3.1337
36.611 | 0.88147 | 107.38 | 0.13909 | 31.26 | 2.4765 | 96.771 | 0.26762 | 38.488 | 3.1672 | 110.21 | 0.33173 | 47.959 | 3.431 | 132.2 | 0.39091 | 69.71 | 2.3557 | 166.39 | 0.41258 | 174.85 | 0.55202 | 322.44 | 0.23267 | 118.86 | 1.6223 | 319.24 | 0.28735 | 117.09 | 3.7428 | 224.51 | 0.91935 | 127.22 | 5.6173 | 258.25 | 1.0278 | 173.8 | 5.8348 | 316.06 | 1.3403 | 252.38 | 3.4104 | 385.65 | 1.4089 | 282.85 | 7.1053 | 399.79 | 2.7486
38.797 | 0.76479 | 119.03 | 0.11837 | 32.601 | 2.1986 | 104.73 | 0.23221 | 39.344 | 2.912 | 119.14 | 0.2877 | 49.767 | 3.0127 | 143.07 | 0.33549 | 72.919 | 2.0665 | 178.1 | 0.36173 | 193.24 | 0.45241 | 355.29 | 0.19734 | 124.58 | 1.4548 | 340.68 | 0.2554 | 122.11 | 3.2734 | 234.38 | 0.84006 | 129.4 | 5.1647 | 270.95 | 0.92996 | 177.85 | 5.2375 | 334.26 | 1.1794 | 258.51 | 3.1107 | 399.39 | 1.2931 | 287.99 | 6.4485 | 414.86 | 2.4659
41.527 | 0.65236 | 132.73 | 0.10242 | 33.796 | 1.9854 | 116.2 | 0.19338 | 40.786 | 2.5698 | 130.24 | 0.24501 | 51.901 | 2.664 | 155.76 | 0.28691 | 76.428 | 1.8073 | 191.97 | 0.31456 | 219.63 | 0.35304 | 382.96 | 0.17379 | 132.15 | 1.2685 | 367.94 | 0.22338 | 126.97 | 2.9004 | 242.97 | 0.77677 | 131.62 | 4.7628 | 285.7 | 0.83422 | 181.8 | 4.7915 | 354.23 | 1.0387 | 269.06 | 2.7534 | 419.44 | 1.1607 | 292.93 | 5.8935 | 429.63 | 2.2328
44.095 | 0.56713 | 146.55 | 0.091779 | 35.564 | 1.7452 | 128.3 | 0.16442 | 42.028 | 2.323 | 141.65 | 0.2115 | 54.02 | 2.3723 | 171.46 | 0.24154 | 80.668 | 1.5634 | 210.68 | 0.26567 | 238.16 | 0.30054 | 412.79 | 0.15387 | 139.9 | 1.1172 | 397.39 | 0.19549 | 131.62 | 2.5905 | 252.88 | 0.71549 | 134.15 | 4.4231 | 300.35 | 0.75271 | 186.41 | 4.3704 | 379.91 | 0.89384 | 277.25 | 2.4989 | 445.83 | 1.005 | 299.44 | 5.306 | 441.83 | 2.0699
47.529 | 0.48039 | 162.44 | 0.082962 | 37.053 | 1.5696 | 140.8 | 0.14085 | 43.308 | 2.1188 | 156.23 | 0.17923 | 56.903 | 2.0377 | 190.44 | 0.20123 | 84.974 | 1.37 | 235.65 | 0.21827 | 260.32 | 0.25179 | 449.41 | 0.13464 | 149 | 0.9732 | 430.49 | 0.17083 | 136.72 | 2.3299 | 267.45 | 0.63939 | 136.86 | 4.0953 | 312.6 | 0.69407 | 190.55 | 4.0182 | 400.59 | 0.79772 | 289.44 | 2.2141 | 473.87 | 0.88259 | 305.8 | 4.83 | 458.49 | 1.8745
50.823 | 0.41472 | 177.39 | 0.076772 | 38.642 | 1.416 | 156.86 | 0.1193 | 45.211 | 1.8754 | 171.29 | 0.15389 | 59.582 | 1.7929 | 207.13 | 0.17475 | 88.885 | 1.22 | 266.23 | 0.17706 | 282.57 | 0.21477 | 491.73 | 0.1171 | 157.74 | 0.86316 | 466.35 | 0.14998 | 141.16 | 2.1337 | 277.81 | 0.59182 | 140.74 | 3.7503 | 328.63 | 0.62955 | 196.75 | 3.6105 | 427.92 | 0.69439 | 300.64 | 1.9914 | 501.66 | 0.78308 | 312.29 | 4.4099 | 482.48 | 1.6323
55.332 | 0.34502 | 201.01 | 0.069472 | 40.219 | 1.2787 | 173.53 | 0.1039 | 47.198 | 1.6567 | 191.01 | 0.12981 | 62.636 | 1.5634 | 225.96 | 0.15128 | 94.57 | 1.0511 | 300.77 | 0.14514 | 303.36 | 0.1869 | 551.11 | 0.10097 | 171.56 | 0.72169 | 498.17 | 0.13502 | 145.9 | 1.9422 | 291.47 | 0.53803 | 145.61 | 3.3563 | 347.21 | 0.56549 | 204.16 | 3.2441 | 445.38 | 0.63768 | 311.04 | 1.82 | 534.29 | 0.68751 | 318.28 | 4.0749 | 510.78 | 1.415
59.761 | 0.29342 | 220.6 | 0.065191 | 41.903 | 1.1593 | 189.49 | 0.094128 | 49.419 | 1.4548 | 221.48 | 0.10474 | 65.258 | 1.4005 | 247.24 | 0.13099 | 100.72 | 0.9056 | 341.84 | 0.11863 | 322.44 | 0.16511 | 596.41 | 0.092744 | 192.28 | 0.57398 | 545.63 | 0.11729 | 150.19 | 1.8073 | 306.72 | 0.48798 | 151.1 | 2.9798 | 372.39 | 0.49327 | 210.59 | 2.9442 | 463.1 | 0.59033 | 322.44 | 1.66 | 560.56 | 0.62364 | 326.99 | 3.6908 | 543.45 | 1.2191
64.932 | 0.24656 | 244.53 | 0.061281 | 43.352 | 1.0659 | 209.84 | 0.084593 | 51.953 | 1.2723 | 248.72 | 0.092308 | 68.879 | 1.2273 | 269.98 | 0.11462 | 107.06 | 0.78887 | 385.04 | 0.10155 | 355.29 | 0.13654 | 644.15 | 0.085955 | 210.17 | 0.4828 | 583.43 | 0.10665 | 155.39 | 1.6567 | 329.95 | 0.42411 | 157.74 | 2.6375 | 415.69 | 0.40187 | 218.1 | 2.6614 | 482.96 | 0.54303 | 333.93 | 1.5141 | 591.07 | 0.56231 | 335.27 | 3.3731 | 569.6 | 1.0921
71.261 | 0.20247 | 265.69 | 0.058623 | 45.438 | 0.95584 | 233.77 | 0.076707 | 54.399 | 1.133 | 273.79 | 0.083789 | 71.833 | 1.1072 | 295.11 | 0.10189 | 113.11 | 0.69617 | 422.14 | 0.091588 | 382.96 | 0.11764 | 709.05 | 0.078625 | 230.66 | 0.40165 | 624.49 | 0.098794 | 160.28 | 1.5263 | 354.58 | 0.36971 | 165.16 | 2.316 | 458.49 | 0.33538 | 224.51 | 2.4421 | 510.78 | 0.48886 | 347.56 | 1.3687 | 623.86 | 0.50596 | 345.48 | 3.0644 | 609.07 | 0.93479
78.598 | 0.1666 | 287.54 | 0.056486 | 47.815 | 0.85116 | 268.63 | 0.068794 | 56.96 | 1.0099 | 303.49 | 0.076446 | 74.84 | 1.0049 | 321.93 | 0.092647 | 121.55 | 0.59502 | 471.7 | 0.082267 | 412.79 | 0.10115 | 768.88 | 0.073417 | 249.37 | 0.34295 | 685.35 | 0.089403 | 166.49 | 1.3935 | 402.19 | 0.29358 | 172.59 | 2.05 | 525.28 | 0.26225 | 231.58 | 2.2185 | 542.9 | 0.43332 | 359.22 | 1.266 | 661.78 | 0.45223 | 358.14 | 2.7562 | 638.38 | 0.8415
87.825 | 0.1333 | 308.07 | 0.054855 | 50.671 | 0.74814 | 298.67 | 0.064057 | 59.88 | 0.89659 | 333.73 | 0.070886 | 79.547 | 0.87183 | 357.22 | 0.083432 | 129.59 | 0.52092 | 521.83 | 0.075174 | 449.41 | 0.085849 | 829.59 | 0.06932 | 275.6 | 0.28079 | 755.16 | 0.081472 | 173.11 | 1.2622 | 441.39 | 0.24871 | 178.92 | 1.8605 | 606.64 | 0.20388 | 239.35 | 2.0256 | 583.43 | 0.38027 | 370.9 | 1.1792 | 723.38 | 0.38708 | 370.16 | 2.4964 | 673.13 | 0.75092
96.965 | 0.10914 | 320.65 | 0.054 | 53.75 | 0.65892 | 330.74 | 0.060372 | 63.329 | 0.78887 | 368.83 | 0.066012 | 84.044 | 0.77093 | 390.08 | 0.077069 | 137.6 | 0.45787 | 569.83 | 0.070091 | 491.73 | 0.071492 | 897.79 | 0.065641 | 294.4 | 0.24557 | 822.98 | 0.075519 | 180.54 | 1.1478 | 485.38 | 0.21083 | 186.03 | 1.6851 | 659.8 | 0.17704 | 246.15 | 1.8754 | 618.89 | 0.34254 | 385.65 | 1.0713 | 805.88 | 0.31858 | 382.96 | 2.2633 | 713.32 | 0.66186
107.38 | 0.089174 | 321 | 0.049 | 57.705 | 0.56374 | 370.31 | 0.057021 | 67.38 | 0.68307 | 405.19 | 0.062239 | 90.138 | 0.65563 | 435 | 0.070565 | 145.96 | 0.40448 | 642.49 | 0.064565 | 551.11 | 0.056974 | 980.37 | 0.062276 | 319.24 | 0.20926 | 898.68 | 0.070432 | 189.41 | 1.0293 | 530.56 | 0.18133 | 193.43 | 1.5293 | 716.9 | 0.15445 | 256.71 | 1.6885 | 663.1 | 0.30223 | 399.39 | 0.98594 | 888.85 | 0.26771 | 399.79 | 2.0074 | 756.67 | 0.58509
119.03 | 0.072355 | 450 | 0.049 | 63.076 | 0.46712 | 403.97 | 0.054953 | 71.332 | 0.60401 | 447.8 | 0.058963 | 98.627 | 0.5384 | 475.49 | 0.066233 | 157.01 | 0.34709 | 703.69 | 0.06116 | 596.41 | 0.048744 | 1053.6 | 0.059841 | 340.68 | 0.18339 | 962.88 | 0.067048 | 201.33 | 0.89748 | 584.02 | 0.15493 | 203.35 | 1.3578 | 764.28 | 0.1395 | 269.6 | 1.4856 | 719.77 | 0.26058 | 419.44 | 0.88501 | 998.18 | 0.21888 | 414.86 | 1.8164 | 801.06 | 0.52002
132.73 | 0.058416 | 641.3 | 0.049 | 69.501 | 0.38054 | 422.99 | 0.054 | 74.989 | 0.54001 | 487.53 | 0.056649 | 107.27 | 0.44971 | 535.04 | 0.061542 | 166.39 | 0.30846 | 807.82 | 0.057034 | 644.15 | 0.041955 | 1151.6 | 0.057271 | 367.94 | 0.15721 | 1042 | 0.06368 | 213.35 | 0.78808 | 648.03 | 0.13134 | 211.65 | 1.2286 | 820.51 | 0.12481 | 282.01 | 1.3376 | 789.13 | 0.22185 | 445.83 | 0.77479 | 1102.1 | 0.18516 | 429.63 | 1.6468 | 866.04 | 0.44316
146.55 | 0.047779 | 641.5 | 0.043 | 74.392 | 0.33016 | 423 | 0.049 | 79.946 | 0.47135 | 526.02 | 0.054855 | 120.34 | 0.35199 | 577.87 | 0.059023 | 178.1 | 0.26816 | 873.36 | 0.055152 | 709.05 | 0.034625 | 1222.8 | 0.055747 | 397.39 | 0.13504 | 1120.9 | 0.061023 | 224.51 | 0.70669 | 708.35 | 0.11477 | 222.5 | 1.0973 | 901.38 | 0.10869 | 297.65 | 1.178 | 866.04 | 0.18898 | 473.87 | 0.67898 | 1196.2 | 0.162 | 441.83 | 1.5278 | 914.09 | 0.39803
162.44 | 0.038962 | 12500 | 0.043 | 79.15 | 0.28963 | 600 | 0.049 | 87.212 | 0.3937 | 548.04 | 0.054 | 132.2 | 0.29021 | 626.62 | 0.05684 | 191.97 | 0.23012 | 921.81 | 0.054 | 768.88 | 0.029417 | 1295.9 | 0.05445 | 430.49 | 0.11496 | 1197.4 | 0.058933 | 234.38 | 0.64522 | 778.94 | 0.10166 | 233.44 | 0.9889 | 954.26 | 0.10178 | 316.06 | 1.0293 | 994.19 | 0.15033 | 501.66 | 0.6016 | 1295.9 | 0.14261 | 458.49 | 1.3949 | 968.68 | 0.35611
177.39 | 0.032772 | 25000 | 0.043 | 84.213 | 0.2556 | 845.98 | 0.049 | 94.855 | 0.33149 | 549 | 0.049 | 143.07 | 0.24705 | 672.73 | 0.055107 | 210.68 | 0.19183 | 922 | 0.049 | 829.59 | 0.02532 | 1326 | 0.054 | 466.35 | 0.097865 | 1277.8 | 0.0571 | 242.97 | 0.5974 | 848.04 | 0.092696 | 244.43 | 0.89569 | 1016.3 | 0.094734 | 334.26 | 0.90923 | 1087.8 | 0.13033 | 534.29 | 0.52826 | 1423.6 | 0.12372 | 482.48 | 1.2298 | 1026.5 | 0.31731
201.01 | 0.025472 |  |  | 89.958 | 0.22287 | 846 | 0.043 | 101.83 | 0.28703 | 750 | 0.049 | 155.76 | 0.20864 | 708.64 | 0.054 | 235.65 | 0.15302 | 1500 | 0.049 | 897.79 | 0.021641 | 1327 | 0.049 | 498.17 | 0.085935 | 1343.4 | 0.055829 | 252.88 | 0.54872 | 926.98 | 0.084796 | 258.25 | 0.796 | 1073.8 | 0.089403 | 354.23 | 0.79919 | 1190.3 | 0.11394 | 560.56 | 0.47847 | 1519.2 | 0.11229 | 510.78 | 1.0723 | 1090 | 0.28303
220.6 | 0.021191 |  |  | 96.771 | 0.1924 | 12500 | 0.043 | 110.21 | 0.24435 | 1096.08 | 0.049 | 171.46 | 0.17236 | 709 | 0.049 | 266.23 | 0.12013 | 1843.62 | 0.049 | 980.37 | 0.018276 | 2000 | 0.049 | 545.63 | 0.071564 | 1396.8 | 0.054964 | 267.45 | 0.49009 | 1010.2 | 0.078384 | 270.95 | 0.71953 | 1127.7 | 0.085165 | 379.91 | 0.68512 | 1298.5 | 0.10155 | 591.07 | 0.42949 | 1632.6 | 0.10253 | 543.45 | 0.92389 | 1183.1 | 0.24301
244.53 | 0.017281 |  |  | 104.73 | 0.16494 | 25000 | 0.043 | 119.14 | 0.20926 | 1097 | 0.043 | 190.44 | 0.13943 | 1100 | 0.049 | 300.77 | 0.093746 | 1844 | 0.043 | 1053.6 | 0.015841 | 2652 | 0.049 | 583.43 | 0.062652 | 1436.5 | 0.054377 | 277.81 | 0.45196 | 1090 | 0.073506 | 285.7 | 0.64522 | 1202.2 | 0.080255 | 400.59 | 0.60947 | 1417.9 | 0.092308 | 623.86 | 0.38939 | 1786.3 | 0.093136 | 569.6 | 0.82848 | 1295.9 | 0.2071
265.69 | 0.014623 |  |  | 116.2 | 0.13277 |  |  | 130.24 | 0.17497 | 12500 | 0.043 | 207.13 | 0.11799 | 1417.28 | 0.049 | 341.84 | 0.072718 | 12500 | 0.043 | 1151.6 | 0.013271 | 2653 | 0.043 | 624.49 | 0.054794 | 1462.5 | 0.054 | 291.47 | 0.41018 | 1185.5 | 0.068968 | 300.35 | 0.58091 | 1265.1 | 0.076805 | 427.92 | 0.53091 | 1573.3 | 0.083197 | 661.78 | 0.34571 | 1942.9 | 0.085454 | 609.07 | 0.71166 | 1435 | 0.17381
287.54 | 0.012486 |  |  | 128.3 | 0.10946 |  |  | 141.65 | 0.14747 | 25000 | 0.043 | 225.96 | 0.099047 | 1418 | 0.043 | 385.04 | 0.057546 | 25000 | 0.043 | 1222.8 | 0.011747 | 12500 | 0.043 | 685.35 | 0.045403 | 1463 | 0.049 | 306.72 | 0.36893 | 1298.4 | 0.064792 | 312.6 | 0.53357 | 1328.7 | 0.073654 | 445.38 | 0.49058 | 1752.7 | 0.075677 | 723.38 | 0.29108 | 2083.8 | 0.080219 | 638.38 | 0.64072 | 1563.9 | 0.15086
308.07 | 0.010855 |  |  | 140.8 | 0.090794 |  |  | 156.23 | 0.12183 |  |  | 247.24 | 0.082318 | 12500 | 0.043 | 422.14 | 0.047588 |  |  | 1295.9 | 0.01045 | 25000 | 0.043 | 755.16 | 0.037472 | 2250 | 0.049 | 329.95 | 0.31977 | 1453.8 | 0.060686 | 328.63 | 0.4828 | 1394 | 0.070939 | 463.1 | 0.45106 | 1915.9 | 0.070485 | 805.88 | 0.23571 | 2221.5 | 0.075868 | 673.13 | 0.57055 | 1709.5 | 0.13097
320.65 | 0.01 |  |  | 156.86 | 0.072791 |  |  | 171.29 | 0.10155 |  |  | 269.98 | 0.06931 | 25000 | 0.043 | 471.7 | 0.038267 |  |  | 1326 | 0.01 |  |  | 822.98 | 0.031519 | 2925 | 0.049 | 354.58 | 0.27578 | 1559.2 | 0.058463 | 347.21 | 0.43424 | 1496.6 | 0.067443 | 482.96 | 0.41347 | 2125.8 | 0.065641 | 888.85 | 0.19395 | 2365.9 | 0.072039 | 713.32 | 0.5025 | 1861.1 | 0.11513
|  |  |  | 173.53 | 0.059895 |  |  | 191.01 | 0.081499 |  |  | 295.11 | 0.057893 |  |  | 521.83 | 0.031174 | [6 empty] | 898.68 | 0.026432 | 2926 | 0.043 | 402.19 | 0.21413 | 1649 | 0.056956 | 372.39 | 0.37638 | 1576.4 | 0.065064 | 510.78 | 0.37077 | 2296 | 0.062571 | 998.18 | 0.15394 | 2542.6 | 0.068376 | 756.67 | 0.4408 | 2067.2 | 0.10092
|  |  |  | 189.49 | 0.050128 |  |  | 221.48 | 0.060739 |  |  | 321.93 | 0.048647 |  |  | 569.83 | 0.026091 | [6 empty] | 962.88 | 0.023048 | 12500 | 0.043 | 441.39 | 0.17797 | 1724.9 | 0.055829 | 415.69 | 0.30145 | 1685.7 | 0.062441 | 542.9 | 0.33016 | 2464.9 | 0.060112 | 1102.1 | 0.1268 | 2787.6 | 0.064299 | 801.06 | 0.39057 | 2246.1 | 0.092019
|  |  |  | 209.84 | 0.040593 |  |  | 248.72 | 0.048308 |  |  | 357.22 | 0.039432 |  |  | 642.49 | 0.020565 | [6 empty] | 1042 | 0.01968 | 25000 | 0.043 | 485.38 | 0.14761 | 1798.9 | 0.05492 | 458.49 | 0.24804 | 1781 | 0.06057 | 583.43 | 0.28589 | 2659.6 | 0.057868 | 1196.2 | 0.10848 | 3025.8 | 0.061194 | 866.04 | 0.33182 | 2509.7 | 0.08269
|  |  |  | 233.77 | 0.032707 |  |  | 273.79 | 0.039789 |  |  | 390.08 | 0.033069 |  |  | 703.69 | 0.01716 | [6 empty] | 1120.9 | 0.017023 |  |  | 530.56 | 0.12367 | 1850 | 0.054325 | 525.28 | 0.18878 | 1893 | 0.058652 | 618.89 | 0.25356 | 2762.6 | 0.056827 | 1295.9 | 0.092628 | 3258.2 | 0.058903 | 914.09 | 0.29489 | 2743.3 | 0.076414
|  |  |  | 268.63 | 0.024794 |  |  | 303.49 | 0.032446 |  |  | 435 | 0.026565 |  |  | 807.82 | 0.013034 | [6 empty] | 1197.4 | 0.014933 |  |  | 584.02 | 0.10206 | 1877.9 | 0.054 | 606.64 | 0.14197 | 1984.1 | 0.057378 | 663.1 | 0.22132 | 2875.3 | 0.055889 | 1423.6 | 0.076906 | 3543.7 | 0.056599 | 968.68 | 0.26076 | 3034.9 | 0.070406
|  |  |  | 298.67 | 0.020057 |  |  | 333.73 | 0.026886 |  |  | 475.49 | 0.022233 |  |  | 873.36 | 0.011152 | [6 empty] | 1277.8 | 0.0131 |  |  | 648.03 | 0.082896 | 1878 | 0.049 | 659.8 | 0.12013 | 2061 | 0.056386 | 719.77 | 0.18784 | 2980.7 | 0.055041 | 1519.2 | 0.067599 | 3800.6 | 0.054942 | 1026.5 | 0.23058 | 3261.4 | 0.06691
|  |  |  | 330.74 | 0.016372 |  |  | 368.83 | 0.022012 |  |  | 535.04 | 0.017542 |  |  | 921.81 | 0.01 | [6 empty] | 1343.4 | 0.011829 |  |  | 708.35 | 0.069588 | 3000 | 0.049 | 716.9 | 0.10155 | 2138.7 | 0.055514 | 789.13 | 0.15612 | 3090 | 0.054336 | 1632.6 | 0.058533 | 3916.4 | 0.054325 | 1090 | 0.2043 | 3536.6 | 0.063503
|  |  |  | 370.31 | 0.013021 |  |  | 405.19 | 0.018239 |  |  | 577.87 | 0.015023 | [10 empty] | 1396.8 | 0.010964 |  |  | 778.94 | 0.057661 | 3755.8 | 0.049 | 764.28 | 0.089442 | 2208.2 | 0.054811 | 866.04 | 0.12936 | 3133.6 | 0.054 | 1786.3 | 0.049136 | 3967.7 | 0.054 | 1183.1 | 0.17271 | 3789.3 | 0.061023
|  |  |  | 403.97 | 0.010953 |  |  | 447.8 | 0.014963 |  |  | 626.62 | 0.01284 | [10 empty] | 1436.5 | 0.010377 |  |  | 848.04 | 0.048696 | 3756 | 0.043 | 820.51 | 0.077913 | 2261.8 | 0.054284 | 994.19 | 0.098651 | 3134 | 0.049 | 1942.9 | 0.041454 | 3968 | 0.049 | 1295.9 | 0.14382 | 4142 | 0.058248
|  |  |  | 422.99 | 0.01 |  |  | 487.53 | 0.012649 |  |  | 672.73 | 0.011107 | [10 empty] | 1462.5 | 0.01 |  |  | 926.98 | 0.040796 | 12500 | 0.043 | 901.38 | 0.064689 | 2289.1 | 0.054 | 1087.8 | 0.082154 | 4500 | 0.049 | 2083.8 | 0.036219 | 6000 | 0.049 | 1435 | 0.11717 | 4354.3 | 0.056879
[8 empty] | 526.02 | 0.010855 |  |  | 708.64 | 0.01 | [14 empty] | 1010.2 | 0.034384 | 25000 | 0.043 | 954.26 | 0.057777 | 2290 | 0.049 | 1190.3 | 0.068758 | 6267.2 | 0.049 | 2221.5 | 0.031868 | 7935.4 | 0.049 | 1563.9 | 0.098651 | 4573 | 0.055688
[8 empty] | 548.04 | 0.01 | [18 empty] | 1090 | 0.029506 |  |  | 1016.3 | 0.050734 | 3000 | 0.049 | 1298.5 | 0.057546 | 6268 | 0.043 | 2365.9 | 0.028039 | 7936 | 0.043 | 1709.5 | 0.082648 | 4731.2 | 0.054931
[28 empty] | 1185.5 | 0.024968 |  |  | 1073.8 | 0.045403 | 4578.2 | 0.049 | 1417.9 | 0.048308 | 12500 | 0.043 | 2542.6 | 0.024376 | 12500 | 0.043 | 1861.1 | 0.069937 | 4855.8 | 0.054377
[28 empty] | 1298.4 | 0.020792 |  |  | 1127.7 | 0.041165 | 4579 | 0.043 | 1573.3 | 0.039197 | 25000 | 0.043 | 2787.6 | 0.020299 | 25000 | 0.043 | 2067.2 | 0.056917 | 4929.2 | 0.054
[28 empty] | 1453.8 | 0.016686 |  |  | 1202.2 | 0.036255 | 12500 | 0.043 | 1752.7 | 0.031677 |  |  | 3025.8 | 0.017194 |  |  | 2246.1 | 0.048019 | 4930 | 0.049
[28 empty] | 1559.2 | 0.014463 |  |  | 1265.1 | 0.032805 | 25000 | 0.043 | 1915.9 | 0.026485 |  |  | 3258.2 | 0.014903 |  |  | 2509.7 | 0.03869 | 7500 | 0.049
[28 empty] | 1649 | 0.012956 |  |  | 1328.7 | 0.029654 |  |  | 2125.8 | 0.021641 |  |  | 3543.7 | 0.012599 |  |  | 2743.3 | 0.032414 | 9858.4 | 0.049
[28 empty] | 1724.9 | 0.011829 |  |  | 1394 | 0.026939 |  |  | 2296 | 0.018571 |  |  | 3800.6 | 0.010942 |  |  | 3034.9 | 0.026406 | 9859 | 0.043
[28 empty] | 1798.9 | 0.01092 |  |  | 1496.6 | 0.023443 |  |  | 2464.9 | 0.016112 |  |  | 3916.4 | 0.010325 |  |  | 3261.4 | 0.02291 | 12500 | 0.043
[28 empty] | 1850 | 0.010325 |  |  | 1576.4 | 0.021064 |  |  | 2659.6 | 0.013868 |  |  | 3967.7 | 0.01 |  |  | 3536.6 | 0.019503 | 25000 | 0.043
[28 empty] | 1877.9 | 0.01 |  |  | 1685.7 | 0.018441 |  |  | 2762.6 | 0.012827 | [6 empty] | 3789.3 | 0.017023
[32 empty] | 1781 | 0.01657 |  |  | 2875.3 | 0.011889 | [6 empty] | 4142 | 0.014248
[32 empty] | 1893 | 0.014652 |  |  | 2980.7 | 0.011041 | [6 empty] | 4354.3 | 0.012879
[32 empty] | 1984.1 | 0.013378 |  |  | 3090 | 0.010336 | [6 empty] | 4573 | 0.011688
[32 empty] | 2061 | 0.012386 |  |  | 3133.6 | 0.01 | [6 empty] | 4731.2 | 0.010931
[32 empty] | 2138.7 | 0.011514 | [10 empty] | 4855.8 | 0.010377
[32 empty] | 2208.2 | 0.010811 | [10 empty] | 4929.2 | 0.01
[32 empty] | 2261.8 | 0.010284
[32 empty] | 2289.1 | 0.01

## 50 Hz, 1320-1 CT Ratio
S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0 | [11 empty] | S&C Vista® Overcurrent Control 2.0
S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed | [11 empty] | S&C K Speed
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018 | [11 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated October 22, 2018
1320:1 CT Ratio | [11 empty] | 1320:1 CT Ratio | [11 empty] | 1320:1 CT Ratio | [11 empty] | 1320:1 CT Ratio | [11 empty] | 1320:1 CT Ratio | [11 empty] | 1320:1 CT Ratio
Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information. | [10 empty] | Tolerance: | See page 36 of S&C Information Bulletin 680-211 for tolerance information.
8K |  |  |  | 10K |  |  |  | 12K |  |  |  | 15K |  |  |  | 20K |  |  |  | 25K |  |  |  | 30K |  |  |  | 40K |  |  |  | 50K |  |  |  | 65K |  |  |  | 80K |  |  |  | 100K |  |  |  | 125K |  |  |  | 150K |  |  |  | 175K |  |  |  | 200K
Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s | Min Trip A | Min Trip s | Total Clear A | Total Clr s
32.896 | 1000 | 39.109 | 1000 | 42.451 | 1000 | 48.684 | 1000 | 49.597 | 1000 | 57.165 | 1000 | 59.915 | 1000 | 67.893 | 1000 | 79.594 | 1000 | 89.205 | 1000 | 97.997 | 1000 | 109.06 | 1000 | 128.37 | 1000 | 143.3 | 1000 | 159.32 | 1000 | 178.03 | 1000 | 195.18 | 1000 | 217.44 | 1000 | 274.55 | 1000 | 312.55 | 1000 | 329.65 | 1000 | 378.1 | 1000 | 401.85 | 1000 | 448.4 | 1000 | 479.75 | 1000 | 570 | 1000 | 329.65 | 1000 | 378.1 | 1000 | 401.85 | 1000 | 448.4 | 1000 | 479.75 | 1000 | 570 | 1000
32.896 | 300.92 | 39.109 | 217.099 | 42.451 | 303.64 | 48.684 | 252.399 | 49.597 | 602.96 | 57.165 | 20.317 | 59.915 | 608.41 | 67.893 | 81.774 | 79.594 | 609.02 | 89.205 | 452.689 | 97.997 | 602.36 | 109.06 | 557.549 | 128.37 | 601.76 | 143.3 | 274.409 | 159.32 | 605.98 | 178.03 | 538.399 | 195.18 | 601.15 | 217.44 | 569.259 | 274.55 | 600 | 312.55 | 170.109 | 329.65 | 600 | 378.1 | 164.259 | 401.85 | 600 | 448.4 | 559.789 | 479.75 | 600 | 570 | 162.329 | 329.65 | 600 | 378.1 | 164.259 | 401.85 | 600 | 448.4 | 559.789 | 479.75 | 600 | 570 | 162.329
32.962 | 270.93 | 39.899 | 64.193 | 42.621 | 261.09 | 49.519 | 118.829 | 49.996 | 26.492 | 58.67 | 14.728 | 60.156 | 161.23 | 69.612 | 40.642 | 79.753 | 578.16 | 90.462 | 246.119 | 98.095 | 568.98 | 110.38 | 322.719 | 128.5 | 569.55 | 145.03 | 129.799 | 159.96 | 559.39 | 181.08 | 308.659 | 195.96 | 553.83 | 220.29 | 351.899 | 275.5 | 300 | 340.1 | 64.209 | 332.5 | 300 | 408.5 | 66.843 | 413.25 | 300 | 482.6 | 150.709 | 494 | 300 | 625.1 | 64.79 | 332.5 | 300 | 408.5 | 66.843 | 413.25 | 300 | 482.6 | 150.709 | 494 | 300 | 625.1 | 64.79
33.061 | 223.15 | 40.705 | 35.116 | 42.835 | 212.91 | 50.62 | 44.571 | 50.599 | 22.04 | 60.336 | 11.532 | 60.336 | 117.2 | 71.517 | 25.39 | 79.913 | 513.81 | 92.752 | 96.975 | 98.389 | 488.26 | 112.05 | 102.719 | 128.5 | 461.21 | 146.78 | 94.061 | 160.44 | 498.62 | 184.37 | 184.099 | 196.75 | 446.68 | 222.95 | 241.709 | 277.4 | 200 | 365.75 | 36.992 | 334.4 | 200 | 446.5 | 35.771 | 422.75 | 200 | 517.75 | 72.508 | 503.5 | 200 | 682.1 | 34.271 | 334.4 | 200 | 446.5 | 35.771 | 422.75 | 200 | 517.75 | 72.508 | 503.5 | 200 | 682.1 | 34.271
33.16 | 181.43 | 41.652 | 22.544 | 43.049 | 167.81 | 51.643 | 27.827 | 51.415 | 18.063 | 62.298 | 9.75 | 60.821 | 88.31 | 73.474 | 18.522 | 80.313 | 422.36 | 94.532 | 61.887 | 98.685 | 424.48 | 113.63 | 66.198 | 128.5 | 359.55 | 148.7 | 69.508 | 161.41 | 415.24 | 187.72 | 113.959 | 197.93 | 362.07 | 225.64 | 185.449 | 287.85 | 100 | 427.5 | 15.999 | 348.65 | 100 | 515.85 | 16.613 | 448.4 | 100 | 555.75 | 39.667 | 530.1 | 100 | 798 | 15.955 | 348.65 | 100 | 515.85 | 16.613 | 448.4 | 100 | 555.75 | 39.667 | 530.1 | 100 | 798 | 15.955
33.226 | 149.58 | 42.664 | 16.085 | 43.222 | 135.08 | 52.844 | 18.748 | 52.349 | 15.224 | 64.582 | 8.3557 | 61.248 | 67.684 | 75.787 | 13.748 | 80.716 | 336.25 | 96.249 | 41.64 | 99.081 | 347.88 | 115.11 | 46.687 | 128.89 | 278.62 | 150.8 | 50.542 | 162.54 | 325.99 | 191.7 | 79.514 | 198.93 | 299.12 | 228.82 | 141.939 | 312.55 | 50 | 513 | 7.4923 | 378.1 | 50 | 617.5 | 7.5333 | 482.6 | 50 | 647.9 | 16.126 | 570 | 50 | 950 | 7.6302 | 378.1 | 50 | 617.5 | 7.5333 | 448.4 | 100 | 647.9 | 16.126 | 570 | 50 | 950 | 7.6302
33.36 | 119.68 | 43.875 | 11.89 | 43.526 | 107.97 | 54.182 | 13.576 | 53.353 | 13.129 | 66.949 | 7.2326 | 61.74 | 54.209 | 77.706 | 11.372 | 81.283 | 255.66 | 98.193 | 29.509 | 99.478 | 282.55 | 116.86 | 33.143 | 129.01 | 216.34 | 152.77 | 38.814 | 163.68 | 258.75 | 195.96 | 54.625 | 200.12 | 251.6 | 232.04 | 112.819 | 340.1 | 30 | 595.65 | 4.3303 | 408.5 | 30 | 717.25 | 4.3265 | 517.75 | 30 | 779 | 7.4607 | 625.1 | 30 | 1102 | 4.3403 | 378.1 | 50 | 717.25 | 4.3265 | 482.6 | 50 | 779 | 7.4607 | 570 | 50 | 1102 | 4.3403
33.493 | 99.768 | 45.076 | 9.4913 | 43.831 | 85.528 | 55.498 | 10.952 | 54.16 | 11.645 | 69.403 | 6.2399 | 62.298 | 43.417 | 80.153 | 9.2222 | 81.69 | 201.51 | 100.08 | 23.27 | 99.677 | 223.6 | 118.74 | 24.695 | 129.4 | 170.69 | 155.23 | 31.524 | 164.83 | 207.03 | 199.92 | 40.811 | 201.33 | 209.11 | 235.32 | 92.087 | 365.75 | 20 | 674.5 | 2.8491 | 446.5 | 20 | 807.5 | 2.8969 | 555.75 | 20 | 902.5 | 4.3537 | 682.1 | 20 | 1244.5 | 2.8708 | 408.5 | 30 | 807.5 | 2.8969 | 517.75 | 30 | 902.5 | 4.3537 | 625.1 | 30 | 1244.5 | 2.8708
33.594 | 81.683 | 46.263 | 7.721 | 43.963 | 69.467 | 56.903 | 8.6711 | 55.42 | 10.205 | 73.401 | 5.2035 | 62.924 | 35.299 | 82.346 | 7.8024 | 82.182 | 155.07 | 102.4 | 18.068 | 99.976 | 173.79 | 120.53 | 20.444 | 129.92 | 141.01 | 158.21 | 24.942 | 166.16 | 159.31 | 203.76 | 30.821 | 203.35 | 178.19 | 238.63 | 76.116 | 427.5 | 10 | 855 | 1.3897 | 515.85 | 10 | 1026 | 1.3856 | 647.9 | 10 | 1035.5 | 2.7579 | 798 | 10 | 1577 | 1.3903 | 446.5 | 20 | 1026 | 1.3856 | 555.75 | 20 | 1035.5 | 2.7579 | 682.1 | 20 | 1577 | 1.3903
33.762 | 67.549 | 47.959 | 6.1808 | 44.272 | 55.249 | 58.46 | 7.2215 | 57.165 | 8.8804 | 77.396 | 4.4028 | 63.493 | 30.412 | 84.769 | 6.6148 | 82.594 | 126.58 | 103.95 | 15.174 | 100.28 | 127.47 | 122.85 | 15.797 | 130.97 | 115.45 | 160.44 | 21.016 | 167.99 | 124.19 | 207.67 | 25.129 | 205.39 | 146.77 | 243.7 | 59.009 | 513 | 5 | 1092.5 | 0.70254 | 617.5 | 5 | 1320.5 | 0.69682 | 779 | 5 | 1301.5 | 1.4053 | 950 | 5 | 2042.5 | 0.69212 | 515.85 | 10 | 1320.5 | 0.69682 | 647.9 | 10 | 1301.5 | 1.4053 | 798 | 10 | 2042.5 | 0.69212
33.932 | 55.693 | 49.767 | 5.074 | 44.538 | 45.597 | 60.18 | 6.0812 | 58.67 | 7.9236 | 81.69 | 3.7816 | 64.067 | 26.466 | 87.438 | 5.7058 | 83.091 | 104.88 | 106.58 | 12.08 | 100.68 | 105.94 | 125.08 | 13.473 | 131.75 | 98.087 | 163.68 | 17.003 | 170.36 | 94.903 | 211.65 | 20.167 | 207.46 | 122.1 | 247.63 | 50.071 | 595.65 | 3 | 1349 | 0.41622 | 717.25 | 3 | 1615 | 0.42094 | 902.5 | 3 | 1681.5 | 0.69394 | 1102 | 3 | 2508 | 0.41891 | 617.5 | 5 | 1615 | 0.42094 | 779 | 5 | 1681.5 | 0.69394 | 950 | 5 | 2508 | 0.41891
34.17 | 45.917 | 51.901 | 4.1153 | 44.941 | 37.146 | 62.075 | 5.1133 | 60.336 | 7.0628 | 84.854 | 3.4244 | 64.906 | 22.507 | 90.734 | 4.9085 | 83.675 | 85.871 | 108.85 | 10.167 | 101.18 | 86.995 | 127.22 | 11.449 | 132.94 | 76.39 | 166.82 | 14.504 | 172.59 | 75.554 | 215.71 | 16.501 | 209.96 | 101.58 | 251.62 | 41.395 | 674.5 | 2 | 1615 | 0.28258 | 807.5 | 2 | 1947.5 | 0.28027 | 1035.5 | 2 | 2061.5 | 0.4197 | 1244.5 | 2 | 2973.5 | 0.28604 | 717.25 | 3 | 1947.5 | 0.28027 | 902.5 | 3 | 2061.5 | 0.4197 | 1102 | 3 | 2973.5 | 0.28604
34.376 | 38.584 | 54.02 | 3.4466 | 45.347 | 29.721 | 64.351 | 4.3759 | 62.298 | 6.2641 | 90.011 | 2.9333 | 65.492 | 19.942 | 94.248 | 4.1819 | 84.6 | 67.145 | 111.27 | 8.5035 | 101.49 | 74.877 | 129.4 | 10.077 | 134.01 | 64.062 | 170.36 | 12.279 | 175.2 | 59.196 | 221.17 | 13.576 | 212.29 | 88.752 | 255.94 | 34.89 | 855 | 1 | 2194.5 | 0.15589 | 1026 | 1 | 2669.5 | 0.15506 | 1301.5 | 1 | 2479.5 | 0.28107 | 1577 | 1 | 4085 | 0.15485 | 807.5 | 2 | 2669.5 | 0.15506 | 1035.5 | 2 | 2479.5 | 0.28107 | 1244.5 | 2 | 4085 | 0.15485
34.756 | 32.683 | 56.903 | 2.8497 | 45.849 | 23.923 | 66.709 | 3.8261 | 64.582 | 5.5392 | 95.196 | 2.5428 | 66.349 | 17.705 | 98.291 | 3.6304 | 85.365 | 52.712 | 113.86 | 7.2896 | 102.3 | 61.121 | 131.62 | 8.9125 | 135.09 | 53.455 | 173.8 | 10.715 | 178.03 | 45.872 | 225.86 | 11.434 | 214.63 | 76.619 | 260.85 | 29 | 1092.5 | 0.5 | 3040 | 0.094 | 1320.5 | 0.5 | 3676.5 | 0.094 | 1681.5 | 0.5 | 3391.5 | 0.15526 | 2042.5 | 0.5 | 5633.5 | 0.094 | 1026 | 1 | 3676.5 | 0.091815 | 1301.5 | 1 | 3391.5 | 0.15526 | 1577 | 1 | 5633.5 | 0.091755
35 | 28.555 | 59.582 | 2.4603 | 46.449 | 20.102 | 69.71 | 3.2546 | 66.949 | 4.9424 | 99.976 | 2.2706 | 67.893 | 14.152 | 102.82 | 3.1778 | 86.395 | 42.985 | 117.09 | 6.1416 | 102.81 | 51.876 | 134.15 | 7.6762 | 136.86 | 40.766 | 177.85 | 9.3575 | 181.08 | 34.843 | 229.97 | 9.9804 | 217.44 | 64.447 | 265.85 | 23.686 | 1349 | 0.3 | 3895 | 0.074 | 1615 | 0.3 | 4655 | 0.074 | 2061.5 | 0.3 | 4702.5 | 0.094 | 2508 | 0.3 | 7172.5 | 0.074 | 1320.5 | 0.5 | 4655 | 0.066685 | 1681.5 | 0.5 | 4702.5 | 0.09152 | 2042.5 | 0.5 | 7172.5 | 0.066489
35.387 | 23.923 | 62.636 | 2.1327 | 47.151 | 16.691 | 72.919 | 2.8399 | 69.403 | 4.4187 | 106.26 | 1.9623 | 69.612 | 11.668 | 107.98 | 2.7653 | 87.089 | 36.739 | 122.11 | 4.9277 | 103.64 | 42.728 | 136.86 | 6.8372 | 138.51 | 34.29 | 181.8 | 8.1299 | 184.37 | 28.47 | 234.38 | 8.6768 | 220.29 | 56.252 | 270.95 | 19.936 | 1615 | 0.2 | 4655 | 0.064 | 1947.5 | 0.2 | 5605 | 0.064 | 2479.5 | 0.2 | 5937.5 | 0.074 | 2973.5 | 0.2 | 8645 | 0.064 | 1615 | 0.3 | 5605 | 0.055 | 2061.5 | 0.3 | 5937.5 | 0.066788 | 2508 | 0.3 | 8645 | 0.055
35.85 | 20.244 | 65.258 | 1.8977 | 47.911 | 14.095 | 76.428 | 2.4776 | 73.401 | 3.7691 | 111.94 | 1.7494 | 71.517 | 9.6296 | 113.17 | 2.4305 | 88.229 | 29.99 | 126.97 | 4.1405 | 104.47 | 35.796 | 140.74 | 5.8794 | 140.18 | 29.161 | 186.41 | 7.0139 | 187.72 | 22.756 | 240.07 | 7.3528 | 222.95 | 48.417 | 277.25 | 16.479 | 2194.5 | 0.1 | 6460 | 0.054 | 2669.5 | 0.1 | 7695 | 0.054 | 3391.5 | 0.1 | 7125 | 0.064 | 4085 | 0.1 | 11970 | 0.054 | 1947.5 | 0.2 | 7695 | 0.045 | 2479.5 | 0.2 | 7125 | 0.055 | 2973.5 | 0.2 | 11970 | 0.045
36.392 | 16.909 | 68.879 | 1.6454 | 48.684 | 12.156 | 80.668 | 2.1306 | 77.396 | 3.2539 | 119.45 | 1.5102 | 73.474 | 8.1079 | 118.86 | 2.1502 | 89.205 | 25.479 | 131.62 | 3.6373 | 105.63 | 29.573 | 145.61 | 4.9607 | 141.73 | 25.942 | 190.55 | 6.2698 | 191.7 | 18.135 | 244.19 | 6.7221 | 225.64 | 42.813 | 282.85 | 14.192 | 3040 | 0.05 | 6461 | 0.049 | 3676.5 | 0.05 | 7696 | 0.049 | 4702.5 | 0.05 | 9880 | 0.054 | 5633.5 | 0.05 | 11971 | 0.049 | 2669.5 | 0.1 | 10500 | 0.045 | 3391.5 | 0.1 | 9880 | 0.045 | 4085 | 0.1 | 16000 | 0.045
36.942 | 14.51 | 71.833 | 1.4726 | 49.519 | 10.515 | 84.974 | 1.8333 | 81.69 | 2.8316 | 128.12 | 1.3035 | 75.787 | 6.7791 | 124.58 | 1.9103 | 90.462 | 21.176 | 136.72 | 3.2281 | 106.58 | 25.326 | 151.1 | 4.2563 | 143.3 | 22.328 | 196.75 | 5.4576 | 195.96 | 15.133 | 252.38 | 5.5737 | 228.82 | 37.034 | 287.99 | 12.381 | 3895 | 0.03 | 9000 | 0.049 | 4655 | 0.03 | 12500 | 0.049 | 5937.5 | 0.03 | 9881 | 0.049 | 7172.5 | 0.03 | 15000 | 0.049 | 3676.5 | 0.05 | 15390 | 0.045 | 4702.5 | 0.05 | 15000 | 0.045 | 5633.5 | 0.05 | 23940 | 0.045
37.5 | 12.589 | 74.84 | 1.3261 | 50.62 | 8.916 | 88.885 | 1.6339 | 84.854 | 2.5724 | 137.13 | 1.1333 | 77.706 | 5.9706 | 132.15 | 1.6489 | 92.752 | 16.23 | 141.16 | 2.924 | 107.66 | 21.908 | 157.74 | 3.6806 | 145.03 | 19.665 | 204.16 | 4.6521 | 199.92 | 12.729 | 258.51 | 4.8869 | 232.04 | 32.068 | 292.93 | 10.889 | 4655 | 0.02 | 12920 | 0.049 | 5605 | 0.02 | 15390 | 0.049 | 7125 | 0.02 | 15000 | 0.049 | 8645 | 0.02 | 23940 | 0.049 | 4655 | 0.03 | 15391 | 0.043 | 5937.5 | 0.03 | 19760 | 0.045 | 7172.5 | 0.03 | 23941 | 0.043
38.029 | 11.267 | 79.547 | 1.1487 | 51.643 | 7.79 | 94.57 | 1.3935 | 90.011 | 2.2341 | 146.93 | 0.98973 | 80.153 | 5.2218 | 139.9 | 1.449 | 94.532 | 13.368 | 145.9 | 2.6611 | 109.06 | 18.706 | 165.16 | 3.1874 | 146.78 | 17.424 | 210.59 | 4.1701 | 203.76 | 10.988 | 269.06 | 4.0808 | 235.32 | 27.711 | 299.44 | 9.4549 | 6460 | 0.01 | 12921 | 0.043 | 7695 | 0.01 | 15391 | 0.043 | 9880 | 0.01 | 19760 | 0.049 | 11970 | 0.01 | 23941 | 0.043 | 5605 | 0.02 | 25000 | 0.043 | 7125 | 0.02 | 19761 | 0.043 | 8645 | 0.02 | 25000 | 0.043
38.565 | 10.164 | 84.044 | 1.0097 | 52.844 | 6.7927 | 100.72 | 1.1932 | 95.196 | 1.9539 | 159.64 | 0.8391 | 82.346 | 4.6499 | 149 | 1.2571 | 96.249 | 11.38 | 150.19 | 2.4379 | 110.38 | 15.972 | 172.59 | 2.7859 | 148.7 | 15.438 | 218.1 | 3.6997 | 207.67 | 9.4863 | 277.25 | 3.5902 | 238.63 | 24.163 | 305.8 | 8.3741 |  |  | 20000 | 0.043 |  |  | 20000 | 0.043 |  |  | 19761 | 0.043 |  |  | 25000 | 0.043 | 7695 | 0.01 |  |  | 9880 | 0.01 | 25000 | 0.043 | 11970 | 0.01
39.109 | 9.1234 | 90.138 | 0.86265 | 54.182 | 5.9289 | 107.06 | 1.0357 | 99.976 | 1.7504 | 174.85 | 0.7064 | 84.769 | 4.1614 | 157.74 | 1.1116 | 98.193 | 9.8143 | 155.39 | 2.2225 | 112.05 | 13.913 | 178.92 | 2.5199 | 150.8 | 13.969 | 224.51 | 3.3655 | 211.65 | 8.3549 | 289.44 | 3.069 | 243.7 | 20.002 | 312.29 | 7.3855 |  |  | 25000 | 0.043 |  |  | 25000 | 0.043 |  |  | 22500 | 0.043
39.899 | 8.0433 | 98.627 | 0.71098 | 55.498 | 5.2218 | 113.11 | 0.91302 | 106.26 | 1.5187 | 193.24 | 0.58568 | 87.438 | 3.7279 | 171.56 | 0.93136 | 100.08 | 8.5066 | 160.28 | 2.0443 | 113.63 | 12.023 | 186.03 | 2.2621 | 152.77 | 12.526 | 231.58 | 3.0773 | 215.71 | 7.3879 | 300.64 | 2.7375 | 247.63 | 17.354 | 318.28 | 6.7235 | [10 empty] | 25000 | 0.043
40.705 | 7.1552 | 107.27 | 0.59403 | 56.903 | 4.6313 | 121.55 | 0.78086 | 111.94 | 1.3551 | 219.63 | 0.462 | 90.734 | 3.3262 | 192.28 | 0.73827 | 102.4 | 7.2852 | 166.49 | 1.8454 | 115.11 | 10.814 | 193.43 | 2.034 | 155.23 | 11.166 | 239.35 | 2.7848 | 221.17 | 6.4292 | 311.04 | 2.4623 | 251.62 | 15.285 | 326.99 | 5.8072
41.652 | 6.3525 | 120.34 | 0.46957 | 58.46 | 4.1489 | 129.59 | 0.68114 | 119.45 | 1.1816 | 238.16 | 0.39836 | 94.248 | 2.9708 | 210.17 | 0.62381 | 103.95 | 6.5133 | 173.11 | 1.6747 | 116.86 | 9.6296 | 203.35 | 1.7887 | 158.21 | 9.9428 | 246.15 | 2.5726 | 225.86 | 5.6908 | 322.44 | 2.2275 | 255.94 | 13.354 | 335.27 | 5.175
42.664 | 5.5892 | 132.2 | 0.39091 | 60.18 | 3.6945 | 137.6 | 0.60104 | 128.12 | 1.0252 | 260.32 | 0.33947 | 98.291 | 2.6349 | 230.66 | 0.52287 | 106.58 | 5.7136 | 180.54 | 1.5062 | 118.74 | 8.5749 | 211.65 | 1.6193 | 160.44 | 8.9338 | 256.71 | 2.2859 | 229.97 | 5.1031 | 333.93 | 2.0323 | 260.85 | 11.552 | 345.48 | 4.5683
43.875 | 4.9177 | 143.07 | 0.33549 | 62.075 | 3.3296 | 145.96 | 0.53504 | 137.13 | 0.88767 | 282.57 | 0.29318 | 102.82 | 2.3463 | 249.37 | 0.4524 | 108.85 | 5.0827 | 189.41 | 1.3473 | 120.53 | 7.7125 | 222.5 | 1.4377 | 163.68 | 7.9633 | 269.6 | 1.9838 | 234.38 | 4.636 | 347.56 | 1.8228 | 265.85 | 10.154 | 358.14 | 3.9367
45.076 | 4.3529 | 155.76 | 0.28691 | 64.351 | 2.9768 | 157.01 | 0.46198 | 146.93 | 0.77402 | 303.36 | 0.25848 | 107.98 | 2.0623 | 275.6 | 0.37606 | 111.27 | 4.5533 | 201.33 | 1.1674 | 122.85 | 6.8953 | 233.44 | 1.2887 | 166.82 | 7.1624 | 282.01 | 1.7669 | 240.07 | 4.1822 | 359.22 | 1.6781 | 270.95 | 9.0507 | 370.16 | 3.5091
46.263 | 3.8878 | 171.46 | 0.24154 | 66.709 | 2.6747 | 166.39 | 0.41258 | 159.64 | 0.65892 | 322.44 | 0.23267 | 113.17 | 1.8255 | 294.4 | 0.33256 | 113.86 | 4.1614 | 213.35 | 1.0272 | 125.08 | 6.1709 | 244.43 | 1.1577 | 170.36 | 6.4163 | 297.65 | 1.5511 | 244.19 | 3.8299 | 370.9 | 1.5543 | 277.25 | 7.8605 | 382.96 | 3.1337
47.959 | 3.431 | 190.44 | 0.20123 | 69.71 | 2.3557 | 178.1 | 0.36173 | 174.85 | 0.55202 | 355.29 | 0.19734 | 118.86 | 1.6223 | 319.24 | 0.28735 | 117.09 | 3.7428 | 224.51 | 0.91935 | 127.22 | 5.6173 | 258.25 | 1.0278 | 173.8 | 5.8348 | 316.06 | 1.3403 | 252.38 | 3.4104 | 385.65 | 1.4089 | 282.85 | 7.1053 | 399.79 | 2.7486
49.767 | 3.0127 | 207.13 | 0.17475 | 72.919 | 2.0665 | 191.97 | 0.31456 | 193.24 | 0.45241 | 382.96 | 0.17379 | 124.58 | 1.4548 | 340.68 | 0.2554 | 122.11 | 3.2734 | 234.38 | 0.84006 | 129.4 | 5.1647 | 270.95 | 0.92996 | 177.85 | 5.2375 | 334.26 | 1.1794 | 258.51 | 3.1107 | 399.39 | 1.2931 | 287.99 | 6.4485 | 414.86 | 2.4659
51.901 | 2.664 | 225.96 | 0.15128 | 76.428 | 1.8073 | 210.68 | 0.26567 | 219.63 | 0.35304 | 412.79 | 0.15387 | 132.15 | 1.2685 | 367.94 | 0.22338 | 126.97 | 2.9004 | 242.97 | 0.77677 | 131.62 | 4.7628 | 285.7 | 0.83422 | 181.8 | 4.7915 | 354.23 | 1.0387 | 269.06 | 2.7534 | 419.44 | 1.1607 | 292.93 | 5.8935 | 429.63 | 2.2328
54.02 | 2.3723 | 247.24 | 0.13099 | 80.668 | 1.5634 | 235.65 | 0.21827 | 238.16 | 0.30054 | 449.41 | 0.13464 | 139.9 | 1.1172 | 397.39 | 0.19549 | 131.62 | 2.5905 | 252.88 | 0.71549 | 134.15 | 4.4231 | 300.35 | 0.75271 | 186.41 | 4.3704 | 379.91 | 0.89384 | 277.25 | 2.4989 | 445.83 | 1.005 | 299.44 | 5.306 | 441.83 | 2.0699
56.903 | 2.0377 | 269.98 | 0.11462 | 84.974 | 1.37 | 266.23 | 0.17706 | 260.32 | 0.25179 | 491.73 | 0.1171 | 149 | 0.9732 | 430.49 | 0.17083 | 136.72 | 2.3299 | 267.45 | 0.63939 | 136.86 | 4.0953 | 312.6 | 0.69407 | 190.55 | 4.0182 | 400.59 | 0.79772 | 289.44 | 2.2141 | 473.87 | 0.88259 | 305.8 | 4.83 | 458.49 | 1.8745
59.582 | 1.7929 | 295.11 | 0.10189 | 88.885 | 1.22 | 300.77 | 0.14514 | 282.57 | 0.21477 | 551.11 | 0.10097 | 157.74 | 0.86316 | 466.35 | 0.14998 | 141.16 | 2.1337 | 277.81 | 0.59182 | 140.74 | 3.7503 | 328.63 | 0.62955 | 196.75 | 3.6105 | 427.92 | 0.69439 | 300.64 | 1.9914 | 501.66 | 0.78308 | 312.29 | 4.4099 | 482.48 | 1.6323
62.636 | 1.5634 | 321.93 | 0.092647 | 94.57 | 1.0511 | 341.84 | 0.11863 | 303.36 | 0.1869 | 596.41 | 0.092744 | 171.56 | 0.72169 | 498.17 | 0.13502 | 145.9 | 1.9422 | 291.47 | 0.53803 | 145.61 | 3.3563 | 347.21 | 0.56549 | 204.16 | 3.2441 | 445.38 | 0.63768 | 311.04 | 1.82 | 534.29 | 0.68751 | 318.28 | 4.0749 | 510.78 | 1.415
65.258 | 1.4005 | 357.22 | 0.083432 | 100.72 | 0.9056 | 385.04 | 0.10155 | 322.44 | 0.16511 | 644.15 | 0.085955 | 192.28 | 0.57398 | 545.63 | 0.11729 | 150.19 | 1.8073 | 306.72 | 0.48798 | 151.1 | 2.9798 | 372.39 | 0.49327 | 210.59 | 2.9442 | 463.1 | 0.59033 | 322.44 | 1.66 | 560.56 | 0.62364 | 326.99 | 3.6908 | 543.45 | 1.2191
68.879 | 1.2273 | 390.08 | 0.077069 | 107.06 | 0.78887 | 422.14 | 0.091588 | 355.29 | 0.13654 | 709.05 | 0.078625 | 210.17 | 0.4828 | 583.43 | 0.10665 | 155.39 | 1.6567 | 329.95 | 0.42411 | 157.74 | 2.6375 | 415.69 | 0.40187 | 218.1 | 2.6614 | 482.96 | 0.54303 | 333.93 | 1.5141 | 591.07 | 0.56231 | 335.27 | 3.3731 | 569.6 | 1.0921
71.833 | 1.1072 | 435 | 0.070565 | 113.11 | 0.69617 | 471.7 | 0.082267 | 382.96 | 0.11764 | 768.88 | 0.073417 | 230.66 | 0.40165 | 624.49 | 0.098794 | 160.28 | 1.5263 | 354.58 | 0.36971 | 165.16 | 2.316 | 458.49 | 0.33538 | 224.51 | 2.4421 | 510.78 | 0.48886 | 347.56 | 1.3687 | 623.86 | 0.50596 | 345.48 | 3.0644 | 609.07 | 0.93479
74.84 | 1.0049 | 475.49 | 0.066233 | 121.55 | 0.59502 | 521.83 | 0.075174 | 412.79 | 0.10115 | 829.59 | 0.06932 | 249.37 | 0.34295 | 685.35 | 0.089403 | 166.49 | 1.3935 | 402.19 | 0.29358 | 172.59 | 2.05 | 525.28 | 0.26225 | 231.58 | 2.2185 | 542.9 | 0.43332 | 359.22 | 1.266 | 661.78 | 0.45223 | 358.14 | 2.7562 | 638.38 | 0.8415
79.547 | 0.87183 | 535.04 | 0.061542 | 129.59 | 0.52092 | 569.83 | 0.070091 | 449.41 | 0.085849 | 897.79 | 0.065641 | 275.6 | 0.28079 | 755.16 | 0.081472 | 173.11 | 1.2622 | 441.39 | 0.24871 | 178.92 | 1.8605 | 606.64 | 0.20388 | 239.35 | 2.0256 | 583.43 | 0.38027 | 370.9 | 1.1792 | 723.38 | 0.38708 | 370.16 | 2.4964 | 673.13 | 0.75092
84.044 | 0.77093 | 577.87 | 0.059023 | 137.6 | 0.45787 | 642.49 | 0.064565 | 491.73 | 0.071492 | 980.37 | 0.062276 | 294.4 | 0.24557 | 822.98 | 0.075519 | 180.54 | 1.1478 | 485.38 | 0.21083 | 186.03 | 1.6851 | 659.8 | 0.17704 | 246.15 | 1.8754 | 618.89 | 0.34254 | 385.65 | 1.0713 | 805.88 | 0.31858 | 382.96 | 2.2633 | 713.32 | 0.66186
90.138 | 0.65563 | 626.62 | 0.05684 | 145.96 | 0.40448 | 703.69 | 0.06116 | 551.11 | 0.056974 | 1053.6 | 0.059841 | 319.24 | 0.20926 | 898.68 | 0.070432 | 189.41 | 1.0293 | 530.56 | 0.18133 | 193.43 | 1.5293 | 716.9 | 0.15445 | 256.71 | 1.6885 | 663.1 | 0.30223 | 399.39 | 0.98594 | 888.85 | 0.26771 | 399.79 | 2.0074 | 756.67 | 0.58509
98.627 | 0.5384 | 672.73 | 0.055107 | 157.01 | 0.34709 | 807.82 | 0.057034 | 596.41 | 0.048744 | 1151.6 | 0.057271 | 340.68 | 0.18339 | 962.88 | 0.067048 | 201.33 | 0.89748 | 584.02 | 0.15493 | 203.35 | 1.3578 | 764.28 | 0.1395 | 269.6 | 1.4856 | 719.77 | 0.26058 | 419.44 | 0.88501 | 998.18 | 0.21888 | 414.86 | 1.8164 | 801.06 | 0.52002
107.27 | 0.44971 | 708.64 | 0.054 | 166.39 | 0.30846 | 873.36 | 0.055152 | 644.15 | 0.041955 | 1222.8 | 0.055747 | 367.94 | 0.15721 | 1042 | 0.06368 | 213.35 | 0.78808 | 648.03 | 0.13134 | 211.65 | 1.2286 | 820.51 | 0.12481 | 282.01 | 1.3376 | 789.13 | 0.22185 | 445.83 | 0.77479 | 1102.1 | 0.18516 | 429.63 | 1.6468 | 866.04 | 0.44316
120.34 | 0.35199 | 709 | 0.049 | 178.1 | 0.26816 | 921.81 | 0.054 | 709.05 | 0.034625 | 1295.9 | 0.05445 | 397.39 | 0.13504 | 1120.9 | 0.061023 | 224.51 | 0.70669 | 708.35 | 0.11477 | 222.5 | 1.0973 | 901.38 | 0.10869 | 297.65 | 1.178 | 866.04 | 0.18898 | 473.87 | 0.67898 | 1196.2 | 0.162 | 441.83 | 1.5278 | 914.09 | 0.39803
132.2 | 0.29021 | 1000 | 0.049 | 191.97 | 0.23012 | 922 | 0.049 | 768.88 | 0.029417 | 1326 | 0.054 | 430.49 | 0.11496 | 1197.4 | 0.058933 | 234.38 | 0.64522 | 778.94 | 0.10166 | 233.44 | 0.9889 | 954.26 | 0.10178 | 316.06 | 1.0293 | 994.19 | 0.15033 | 501.66 | 0.6016 | 1295.9 | 0.14261 | 458.49 | 1.3949 | 968.68 | 0.35611
143.07 | 0.24705 | 1417.28 | 0.049 | 210.68 | 0.19183 | 1500 | 0.049 | 829.59 | 0.02532 | 1327 | 0.049 | 466.35 | 0.097865 | 1277.8 | 0.0571 | 242.97 | 0.5974 | 848.04 | 0.092696 | 244.43 | 0.89569 | 1016.3 | 0.094734 | 334.26 | 0.90923 | 1087.8 | 0.13033 | 534.29 | 0.52826 | 1423.6 | 0.12372 | 482.48 | 1.2298 | 1026.5 | 0.31731
155.76 | 0.20864 | 1418 | 0.043 | 235.65 | 0.15302 | 1843.62 | 0.049 | 897.79 | 0.021641 | 2000 | 0.049 | 498.17 | 0.085935 | 1343.4 | 0.055829 | 252.88 | 0.54872 | 926.98 | 0.084796 | 258.25 | 0.796 | 1073.8 | 0.089403 | 354.23 | 0.79919 | 1190.3 | 0.11394 | 560.56 | 0.47847 | 1519.2 | 0.11229 | 510.78 | 1.0723 | 1090 | 0.28303
171.46 | 0.17236 | 12500 | 0.043 | 266.23 | 0.12013 | 1844 | 0.043 | 980.37 | 0.018276 | 2652 | 0.049 | 545.63 | 0.071564 | 1396.8 | 0.054964 | 267.45 | 0.49009 | 1010.2 | 0.078384 | 270.95 | 0.71953 | 1127.7 | 0.085165 | 379.91 | 0.68512 | 1298.5 | 0.10155 | 591.07 | 0.42949 | 1632.6 | 0.10253 | 543.45 | 0.92389 | 1183.1 | 0.24301
190.44 | 0.13943 | 25000 | 0.043 | 300.77 | 0.093746 | 12500 | 0.043 | 1053.6 | 0.015841 | 2653 | 0.043 | 583.43 | 0.062652 | 1436.5 | 0.054377 | 277.81 | 0.45196 | 1090 | 0.073506 | 285.7 | 0.64522 | 1202.2 | 0.080255 | 400.59 | 0.60947 | 1417.9 | 0.092308 | 623.86 | 0.38939 | 1786.3 | 0.093136 | 569.6 | 0.82848 | 1295.9 | 0.2071
207.13 | 0.11799 |  |  | 341.84 | 0.072718 | 25000 | 0.043 | 1151.6 | 0.013271 | 12500 | 0.043 | 624.49 | 0.054794 | 1462.5 | 0.054 | 291.47 | 0.41018 | 1185.5 | 0.068968 | 300.35 | 0.58091 | 1265.1 | 0.076805 | 427.92 | 0.53091 | 1573.3 | 0.083197 | 661.78 | 0.34571 | 1942.9 | 0.085454 | 609.07 | 0.71166 | 1435 | 0.17381
225.96 | 0.099047 |  |  | 385.04 | 0.057546 |  |  | 1222.8 | 0.011747 | 25000 | 0.043 | 685.35 | 0.045403 | 1463 | 0.049 | 306.72 | 0.36893 | 1298.4 | 0.064792 | 312.6 | 0.53357 | 1328.7 | 0.073654 | 445.38 | 0.49058 | 1752.7 | 0.075677 | 723.38 | 0.29108 | 2083.8 | 0.080219 | 638.38 | 0.64072 | 1563.9 | 0.15086
247.24 | 0.082318 |  |  | 422.14 | 0.047588 |  |  | 1295.9 | 0.01045 |  |  | 755.16 | 0.037472 | 2250 | 0.049 | 329.95 | 0.31977 | 1453.8 | 0.060686 | 328.63 | 0.4828 | 1394 | 0.070939 | 463.1 | 0.45106 | 1915.9 | 0.070485 | 805.88 | 0.23571 | 2221.5 | 0.075868 | 673.13 | 0.57055 | 1709.5 | 0.13097
269.98 | 0.06931 |  |  | 471.7 | 0.038267 |  |  | 1326 | 0.01 |  |  | 822.98 | 0.031519 | 2925 | 0.049 | 354.58 | 0.27578 | 1559.2 | 0.058463 | 347.21 | 0.43424 | 1496.6 | 0.067443 | 482.96 | 0.41347 | 2125.8 | 0.065641 | 888.85 | 0.19395 | 2365.9 | 0.072039 | 713.32 | 0.5025 | 1861.1 | 0.11513
295.11 | 0.057893 |  |  | 521.83 | 0.031174 | [6 empty] | 898.68 | 0.026432 | 2956 | 0.043 | 402.19 | 0.21413 | 1649 | 0.056956 | 372.39 | 0.37638 | 1576.4 | 0.065064 | 510.78 | 0.37077 | 2296 | 0.062571 | 998.18 | 0.15394 | 2542.6 | 0.068376 | 756.67 | 0.4408 | 2067.2 | 0.10092
321.93 | 0.048647 |  |  | 569.83 | 0.026091 | [6 empty] | 962.88 | 0.023048 | 12500 | 0.043 | 441.39 | 0.17797 | 1724.9 | 0.055829 | 415.69 | 0.30145 | 1685.7 | 0.062441 | 542.9 | 0.33016 | 2464.9 | 0.060112 | 1102.1 | 0.1268 | 2787.6 | 0.064299 | 801.06 | 0.39057 | 2246.1 | 0.092019
357.22 | 0.039432 |  |  | 642.49 | 0.020565 | [6 empty] | 1042 | 0.01968 | 25000 | 0.043 | 485.38 | 0.14761 | 1798.9 | 0.05492 | 458.49 | 0.24804 | 1781 | 0.06057 | 583.43 | 0.28589 | 2659.6 | 0.057868 | 1196.2 | 0.10848 | 3025.8 | 0.061194 | 866.04 | 0.33182 | 2509.7 | 0.08269
390.08 | 0.033069 |  |  | 703.69 | 0.01716 | [6 empty] | 1120.9 | 0.017023 |  |  | 530.56 | 0.12367 | 1850 | 0.054325 | 525.28 | 0.18878 | 1893 | 0.058652 | 618.89 | 0.25356 | 2762.6 | 0.056827 | 1295.9 | 0.092628 | 3258.2 | 0.058903 | 914.09 | 0.29489 | 2743.3 | 0.076414
435 | 0.026565 |  |  | 807.82 | 0.013034 | [6 empty] | 1197.4 | 0.014933 |  |  | 584.02 | 0.10206 | 1877.9 | 0.054 | 606.64 | 0.14197 | 1984.1 | 0.057378 | 663.1 | 0.22132 | 2875.3 | 0.055889 | 1423.6 | 0.076906 | 3543.7 | 0.056599 | 968.68 | 0.26076 | 3034.9 | 0.070406
475.49 | 0.022233 |  |  | 873.36 | 0.011152 | [6 empty] | 1277.8 | 0.0131 |  |  | 648.03 | 0.082896 | 1878 | 0.049 | 659.8 | 0.12013 | 2061 | 0.056386 | 719.77 | 0.18784 | 2980.7 | 0.055041 | 1519.2 | 0.067599 | 3800.6 | 0.054942 | 1026.5 | 0.23058 | 3261.4 | 0.06691
535.04 | 0.017542 |  |  | 921.81 | 0.01 | [6 empty] | 1343.4 | 0.011829 |  |  | 708.35 | 0.069588 | 3000 | 0.049 | 716.9 | 0.10155 | 2138.7 | 0.055514 | 789.13 | 0.15612 | 3090 | 0.054336 | 1632.6 | 0.058533 | 3916.4 | 0.054325 | 1090 | 0.2043 | 3536.6 | 0.063503
577.87 | 0.015023 | [10 empty] | 1396.8 | 0.010964 |  |  | 778.94 | 0.057661 | 3755.8 | 0.049 | 764.28 | 0.089442 | 2208.2 | 0.054811 | 866.04 | 0.12936 | 3133.6 | 0.054 | 1786.3 | 0.049136 | 3967.7 | 0.054 | 1183.1 | 0.17271 | 3789.3 | 0.061023
626.62 | 0.01284 | [10 empty] | 1436.5 | 0.010377 |  |  | 848.04 | 0.048696 | 3756 | 0.043 | 820.51 | 0.077913 | 2261.8 | 0.054284 | 994.19 | 0.098651 | 3134 | 0.049 | 1942.9 | 0.041454 | 3968 | 0.049 | 1295.9 | 0.14382 | 4142 | 0.058248
672.73 | 0.011107 | [10 empty] | 1462.5 | 0.01 |  |  | 926.98 | 0.040796 | 12500 | 0.043 | 901.38 | 0.064689 | 2289.1 | 0.054 | 1087.8 | 0.082154 | 4500 | 0.049 | 2083.8 | 0.036219 | 6000 | 0.049 | 1435 | 0.11717 | 4354.3 | 0.056879
708.64 | 0.01 | [14 empty] | 1010.2 | 0.034384 | 25000 | 0.043 | 954.26 | 0.057777 | 2290 | 0.049 | 1190.3 | 0.068758 | 6267.2 | 0.049 | 2221.5 | 0.031868 | 7935.4 | 0.049 | 1563.9 | 0.098651 | 4573 | 0.055688
[16 empty] | 1090 | 0.029506 |  |  | 1016.3 | 0.050734 | 3000 | 0.049 | 1298.5 | 0.057546 | 6268 | 0.043 | 2365.9 | 0.028039 | 7936 | 0.043 | 1709.5 | 0.082648 | 4731.2 | 0.054931
[16 empty] | 1185.5 | 0.024968 |  |  | 1073.8 | 0.045403 | 4578.2 | 0.049 | 1417.9 | 0.048308 | 12500 | 0.043 | 2542.6 | 0.024376 | 12500 | 0.043 | 1861.1 | 0.069937 | 4855.8 | 0.054377
[16 empty] | 1298.4 | 0.020792 |  |  | 1127.7 | 0.041165 | 4579 | 0.043 | 1573.3 | 0.039197 | 25000 | 0.043 | 2787.6 | 0.020299 | 25000 | 0.043 | 2067.2 | 0.056917 | 4929.2 | 0.054
[16 empty] | 1453.8 | 0.016686 |  |  | 1202.2 | 0.036255 | 12500 | 0.043 | 1752.7 | 0.031677 |  |  | 3025.8 | 0.017194 |  |  | 2246.1 | 0.048019 | 4930 | 0.049
[16 empty] | 1559.2 | 0.014463 |  |  | 1265.1 | 0.032805 | 25000 | 0.043 | 1915.9 | 0.026485 |  |  | 3258.2 | 0.014903 |  |  | 2509.7 | 0.03869 | 7500 | 0.049
[16 empty] | 1649 | 0.012956 |  |  | 1328.7 | 0.029654 |  |  | 2125.8 | 0.021641 |  |  | 3543.7 | 0.012599 |  |  | 2743.3 | 0.032414 | 9858.4 | 0.049
[16 empty] | 1724.9 | 0.011829 |  |  | 1394 | 0.026939 |  |  | 2296 | 0.018571 |  |  | 3800.6 | 0.010942 |  |  | 3034.9 | 0.026406 | 9859 | 0.043
[16 empty] | 1798.9 | 0.01092 |  |  | 1496.6 | 0.023443 |  |  | 2464.9 | 0.016112 |  |  | 3916.4 | 0.010325 |  |  | 3261.4 | 0.02291 | 12500 | 0.043
[16 empty] | 1850 | 0.010325 |  |  | 1576.4 | 0.021064 |  |  | 2659.6 | 0.013868 |  |  | 3967.7 | 0.01 |  |  | 3536.6 | 0.019503 | 25000 | 0.043
[16 empty] | 1877.9 | 0.01 |  |  | 1685.7 | 0.018441 |  |  | 2762.6 | 0.012827 | [6 empty] | 3789.3 | 0.017023
[20 empty] | 1781 | 0.01657 |  |  | 2875.3 | 0.011889 | [6 empty] | 4142 | 0.014248
[20 empty] | 1893 | 0.014652 |  |  | 2980.7 | 0.011041 | [6 empty] | 4354.3 | 0.012879
[20 empty] | 1984.1 | 0.013378 |  |  | 3090 | 0.010336 | [6 empty] | 4573 | 0.011688
[20 empty] | 2061 | 0.012386 |  |  | 3133.6 | 0.01 | [6 empty] | 4731.2 | 0.010931
[20 empty] | 2138.7 | 0.011514 | [10 empty] | 4855.8 | 0.010377
[20 empty] | 2208.2 | 0.010811 | [10 empty] | 4929.2 | 0.01
[20 empty] | 2261.8 | 0.010284
[20 empty] | 2289.1 | 0.01